|  | UST Cathodic Protection System Evaluation Galvanic (Sacrificial Anode) Type Underground Storage Tanks (UST) Program Doc Type: Compliance Certification |
| --- | --- |

Instructions:  Within 30 days, send completed form to Joann Henry, Minnesota Pollution Control Agency (MCPA) at the address above, fax to 651-297-2343, or e-mail joann.henry@state.mn.us.

- All reports must be submitted regardless of results (pass, fail, or inconclusive)

- Incomplete, unsigned, or illegible forms will not be accepted and will be returned.

| ### 1. UST facility |  |  |  |  |  |  | ### MPCA Site ID #: |  |  |  |  |  |  |  |  |  |  |  |  | ### 2. UST owner/operator |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  |  |  |  |  |  | Zip code: |  |  |  |  |  | City: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | State: |  |  |  |  |
| County: |  |  |  |  |  |  |  |  |  | Phone: |  |  |  |  |  |  |  |  |  | Zip code: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Phone: |  |  |  |  |  |  |
| Contact name (if different than above): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Contact phone: |  |  |  |  |  |  |  |  |  |  |  |  |
| ### 3. Cathodic Protection (CP) tester information and qualifications |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tester name (print): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Company name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | City: |  |  |  |  |  |  |  |  |  |  |  |
| State: |  |  |  |  | Zip code: |  |  |  |  |  |  |  |  |  |  | Phone: |  |  |  |  |  |  |  |  |  |  |  |  |  | E-mail: |  |  |  |  |  |  |  |  |  |  |  |
| National Association of Corrosion Engineers (NACE) international certification #: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Steel Tank Institute (STI) certification #: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### 4. Reason survey was conducted (check only one) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Routine - 3 years Routine - within 6 months of install 30-day re-survey after fail Re-survey within 6 months of repair/modification |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Date next CP survey must be conducted by (mm/dd/yyyy): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ### (Required within 6 months of install or repair, and every 3 years thereafter.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### 5. CP tester’s evaluation (check only one) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Pass All protected structures at this facility pass the CP survey and the continuity survey indicates all protected structures are isolated. It is judged that adequate CP has been provided to the UST system (Complete sections 7 and 8). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fail One or more protected structures at this facility fail the CP survey, and it is judged that adequate CP has not been provided to the UST system. (Complete sections 7 and 8). Inconclusive The remote and the local do not both indicate the same test result on all protected structures (both pass or both fail),or the continuity survey indicates continuous or inconclusive results when compared to non-protected structures, the survey must be evaluated by a corrosion expert (Corrosion Expert to complete section 6). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CP Tester Signature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date CP survey performed (mm/dd/yyyy): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. Corrosion expert’s evaluation (if applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The attached survey must be conducted and/or evaluated by a corrosion expert when: a) conducting repairs to metallic structures which are non-factory coated with dielectric material; b) adding supplemental anodes to the tanks and/or piping without following accepted industry standards; c) the local and remote structure-to-soil potential did not result in the same outcome (both pass or both fail); d) the continuity survey indicates one or more of the protected structures are not isolated; e) when required by MPCA (Corrosion Expert to complete sections 7 and 8). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Pass All protected structures at this facility have been judged that the adequate CP is provided to the UST system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fail One or more protected structures at this facility fail the CP survey and it is judged that adequate CP has not been provided to the UST system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrosion expert’s name (print): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Phone: |  |  |  |  |  |  |  |  |  |  |
| Company name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NACE Int./PE certification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NACE Int./PE certification #: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CP Expert Signature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date (mm/dd/yyyy): |  |  |  |  |  |  |  |  |  |
| 7. Criteria applicable to evaluation (check all that apply) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| -850 On Structure-to-soil potential more negative than -850 millivolts (mV) with the protective current applied. -850 Off Structure-to-soil potential more negative than -850 mV with the protective current momentarily interrupted. (“Instant Off”) 100 mV Structure tested exhibits at least 100 mV of cathodic polarization. (“Instant Off “ readings minus native/depol readings) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Facility name: |  | Date of test (mm/dd/yyyy): |  |
| --- | --- | --- | --- |

(Note: The facility name and date of test will automatically populate from page one, if filled out electronically.)

### 8. Action required as a result of this evaluation (check only one)

None CP is adequate. No further action is necessary at this time. Test again by no later than (see Section 4). Retest CP may not be adequate. Retest within 30 days to determine if passing results can be achieved. (Retests may occur only if all protected structures are isolated from non-protected structures) Repair & Retest CP is not adequate. Repair/modification is necessary within the next 60 days, or permanently close the tank system.

| ### 9. CP system repairs and/or modification information |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - Date of “failing” test: |  |  |  |  |  | - Date of repair: |  |  | - Repair company: |  |  |  |
|  |  |  |  | - (mm/dd/yyyy) |  |  | - (mm/dd/yyyy) |  |  |  |  |  |
| - Name of lead repair technician: |  |  |  |  |  |  |  |  |  | - Phone # |  |  |
| - Certification of repair technician (check all that apply): Steel Tank Institute NACE MPCA certified supervisor - Note: submit failing test results with this report if not already submitted. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Description of Repairs (check all that apply) |  |  |  |  |  |  |  |  |  |  |  |
|  | - 1. Supplemental anodes for a sti-P3® tank. |  |  |  |  |  |  | - Repairs /modifications for 1 & 2 must be designed by a “corrosion expert” or installed per industry standards. Attach corrosion experts design, or documentation industry standard was followed. (Section 6 must be signed if designed by a corrosion expert.) |  |  |  |  |
|  | - 2. Supplemental anodes for metallic pipe which is factory coated with dielectirc material (fusion bonded epoxy or equivilent). |  |  |  |  |  |  |  |  |  |  |  |
|  | - 3. Supplemental anodes for a non-sti-P3® tank. (e.g., bare steel). |  |  |  |  |  |  | Repairs/modifications for 3 & 4 and must be designed and evaluated by a corrosion expert only. Attach a corrosion experts design. (Section 6 must be signed.) |  |  |  |  |
|  | - 4. Supplimental anodes for metalic pipe which is non-factory coated with dielectirc material (e.g., galvanized, copper, bare steel, etc.). |  |  |  |  |  |  |  |  |  |  |  |
|  | - 5. Isolation of Galvanically protected tanks/piping. (explain in “remarks/other” below). |  |  |  |  |  |  |  |  |  |  |  |
|  | - 6. Isolation of non-protected metal pipe segments (e.g., flex connectors) at STP or dispenser sumps (explain in “remarks/other” below). |  |  |  |  |  |  |  |  |  |  |  |
| - Remarks/Other: |  |  |  |  |  |  |  |  |  |  |  |  |

### 10.	Galvanic (sacrificial anode) structure to soil potential and continuity survey

Half Cell Placement (testing) on frozen soil, concrete, asphalt, or other paving materials is not acceptable.

Structure to Soil Potentials:

- The half cell must be placed in a minimum of three locations per tank, and three locations per piping run. At least one of the reference cell locations must be in the soil directly over the tested structure (local); and at least one must be placed in soil approximately 25 to100 feet away from the structure (remote). The third location is at the discretion of the tester (either local or remote).

- When testing flex connectors only, two tests points are required for each flex connector, one local and one remote.

- Both the local and the remote voltage must meet one of the three criteria listed in section 7 in order for the structure to pass. Inconclusive must be indicated when both the local and the remote structure-to-soil potentials do not result in the same outcome (both pass or both fail).

- If the “-850 mV Off” or the “100 mV Polarization” criteria is used for galvanic systems, record structure-to-soil potential readings on the MPCA Impressed Current data sheet or similar form.

Continuity Testing: (Point-to-Point and/or Fixed Cell-Moving Ground)

- Point-to-Point: When conducting this method, the leads of the volt meter are required to contact the two structures being examined to demonstrate isolation or continuity. A half cell is not used for this test method.

- Fixed Cell-Moving Ground: When conducting this method, the half cell must be placed in the soil at a remote location approximately 25 to100 feet away and left undisturbed. The other lead of the meter is moved to structures being evaluated.

- To interpret continuity data for either method compare the difference in voltage of the structures evaluated and use the following guidelines: 1 mV or less = continuous, 1-10 mV= inconclusive, greater than 10 mV = isolated.

- For galvanic systems, the structure that is to be protected must be isolated from all other non-protected metallic structure in order to “pass” the continuity survey.

- If other approved continuity testing methods are used, alter this form or submit the data on a separate sheet.

| Facility name: |  | Date of test (mm/dd/yyyy): |  |
| --- | --- | --- | --- |

(Note: The facility name and date of test will automatically populate from page one, if filled out electronically.)

| Describe soil type and location(s) of remote reference cell placement(s) (e.g., Black Dirt, 30 feet NW of Tank #1 spill bucket): |  |
| --- | --- |
| Remote location #1: |  |
| Remote location #2: |  |
| Describe soil type(s) of local reference cell placements: |  |

|  | Structure to soil potentials (mV) |  |  | Continuity testing (mV) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Half cell site map code | Half cell placement description | “ON” Voltage | Structure tested | Point-to- point voltage | Fixed cell remote voltage | Isolated/ Continuous/ Inconclusive |
| Structure : (Example) Tank 1 | (Ex)1 | Local, soil at ATG manway | -1011 mV | (Ex) ATG Conduit | 475 mV |  | isolated |
|  | (Ex)2 | Local, Soil at STP manway | -995 mV | (Ex) STP conduit |  | -528 mV | isolated |
|  | (Ex)R-1 | Remote #1 | -1042 mV | (Ex) Vent | 421 mV |  | isolated |
|  | Structure contact point(s): (Ex)Tank Bottom |  |  | (Ex) Fill Riser | 375 mV | -522 mV | isolated |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |

| Facility name: |  | Date of test (mm/dd/yyyy): |  |
| --- | --- | --- | --- |

(Note: The facility name and date of test will automatically populate from page one, if filled out electronically.)

|  | Structure to soil potentials (mV) |  |  |  | Continuity testing (mV) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Half cell site map code | Half cell placement description | “ON” Voltage |  | Structure tested | Point-to- point voltage | Fixed cell remote voltage | Isolated/ Continuous/ Inconclusive |
| Structure: |  |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |  |
| Structure: |  |  |  |  |  |  |  |  |
|  | Structure contact point(s): |  |  |  |  |  |  |  |
|  | Overall Structure Results (Structure to soil potentials and continuity): Pass Fail Inconclusive |  |  |  |  |  |  |  |

Comments/Remarks:

If separate corrosion protection is required on flex connectors, treat each flex as if it were an individual metal pipe.

Attach additional sheets as needed.

| Facility name: |  | Date of test (mm/dd/yyyy): |  |
| --- | --- | --- | --- |

(Note: The facility name and date of test will automatically populate from page one, if filled out electronically.)

| 11. Description of UST system |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Tank/ Pipe # | Product | Capacity (Gallons) |  | Tank type1 | Piping type 2 | Metal Segments at Tank sump 3 | Metal Segments at Dispenser3 |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |
| Ex: | Premium | 10,000 |  | SW sti-P3®, | DW Fiberglass | CP w/ anodes | In Containment |
| - Indicate if tank is Double Wall (DW) or Single Wall (SW). Also indicated type (e.g., steel, fiberglass, sti-P3®, composite etc.). Also indicate if tank is compartmental if applicable - Indicate if piping is Double Wall (DW) or Single Wall (SW). Also indicate type (e.g., coated steel, fiberglass, galvanized, flex, etc.). - Indicate how metal segments such as flex connectors or metal pipe segments are protected from corrosion (e.g., isolated, booted, bonded, CP w/anodes, in containment, etc.) |  |  |  |  |  |  |  |
| ### 12. UST facility site drawing |  |  |  |  |  |  |  |

Attach detailed drawing or use the space provided to draw a sketch of the UST and CP systems. At a minimum you should indicate the following: All tanks, piping and dispensers; Location of anodes if known; All buildings and streets; Location of CP test stations; Each reference cell placement (local and remote) must be indicated by a code (e.g., 1,2, T-1,) corresponding with the appropriate test in Section 10 of this form. If supplemental anodes are added to the tank system, indicate number, size, location and depth of the new anodes. An evaluation of the CP system is not complete without an acceptable site drawing.

[Indicate North Here]