## Instructions
General information
This analysis spreadsheet is a tool for evaluation of wastewater treatment plant design data. A detailed analysis of existing flow conditions and the use of adequate flow estimates will determine the hydraulic and pollutant removal capacity needed to properly treat the wastewater and comply with permit conditions. Refer to the Minnesota Pollution Control Agency (MPCA) guidance document Design flow and loading determination. Guidelines for Wastewater Treatment Plants (wq-wwtp5-20) for definitions, background, Table 1, and further details. This guidance document can be found on the MPCA website at:
https://www.pca.state.mn.us/business-with-us/engineering-and-technical-information-for-construction-or-expansion
Instructions
For a mechanical plant with an existing sanitary sewer system, the tab Design Flows - Table 2 must be used to determine the peak hourly wet weather flow, the peak instantaneous wet weather flow, the average dry weather flow, and the average wet weather flow. Design Loadings - Table 3 is not a required submittal. Other methods of determining design loadings are acceptable, but must be attached with this form. Design loadings in pounds per day (#/day) must be entered in Summary Table 4.
To use this spreadsheet, follow the steps detailed below. The proper input location for each step is identified on the worksheets where appropriate. All input locations are shaded blue or green to distinguish them from calculation cells in the worksheets.
Step 1: Input the facility data into the Design Flows - Table 2 worksheet (see tab on bottom bar below). This information will automatically be carried forward to the Design Loadings - Table 3 worksheet and Summary Table 4.
Step 2: Input the flow data into the Design Flows - Table 2 worksheet. Use the Source column to indicate where the data came from.
Step 3: Input the Unit Basis into the Design Loadings - Table 3 worksheet. Table 3 is not a required submittal. Other methods of determining design loadings are acceptable, but must be attached with this form. Design loadings in pounds per day (#/day) must be entered in Summary Table 4.
Step 4: Input the average dry weather (ADW) and average wet weather (AWW) data into the Design Loadings - Table 3 worksheet.
Step 5: Input the design loadings in #/day to Summary Table 4. Table 2 and Table 4 are required submittals for Facility Plan approval with documentation used to determine loadings attached.
Design flow and loading determination worksheets
Municipal/Industrial Wastewater
Doc Type: Engineering Report
wq-wwtp5-20a (Revised 3/2/23)

## Design Flows - Table 2
Design flow determination worksheet
| Project name: | [6 empty] | Text input cell - green
| Location: | [6 empty] | Number input cell - blue
|  | Completed by: |  |  | Date: |  |  | Calculation cell - no color
Consultant:
(A) Determination of peak hourly wet weather design flows (PHWW): | [6 empty] | action | Gallons per day | Source | MGD
1 | Present peak hourly dry weather flow | [7 empty] | DMR Data | 0.105 | 105000
2 | Present peak hourly flow during high ground water period (no runoff) | [7 empty] | Estimate | 0.135 | 135000
3 | Present peak hourly dry weather flow [same as (1)] | [5 empty] | - | 0 |  | 0.105
4 | Present peak hourly infiltration [(2)-(4) | [5 empty] | = | 0 | Estimate | 0.03
5 | Present hourly flow during high ground water period and runoff at point of greatest distance between Curves Y and Z | [7 empty] | Estimate | 0.249 | 249000
6 | Present hourly flow during high ground water (no runoff) at same time of day as (5) measurement | [5 empty] | - |  | Estimate | 0.135 | 135000
7 | Present peak hourly inflow | [5 empty] | = | 0 | Estimate | 0.114
8 | Present peak hourly inflow adjusted for a 5-year 1-hour rainfall event | [7 empty] | Estimate | 0.114 | 114000
9 | Present peak hourly infiltration [same as (4)] | [6 empty] | 0 | Estimate | 0.03
10 | Peak hourly infiltration cost effective to eliminate | [5 empty] | - |  |  | 0 | 0
11 | Peak hourly infiltration after rehabilitation (where rehabilitation is cost effective) | [5 empty] | = | 0 | Estimate | 0.03
12 | Present peak hourly adjusted inflow [same as (8)] | [7 empty] | Estimate | 0.114 | 114000
13 | Peak hourly inflow cost effective to eliminate | [5 empty] | - |  |  | 0 | 0
14 | Peak hourly inflow after rehabilitation (where rehabilitation is cost effective) | [5 empty] | = | 0 | Estimate | 0.114
15 | Population increase: |  | persons | @ |  | gpcd multiplied by 2.5 (peaking factor) |  | 0 |  | 0
16 | Peak hourly flow from planned industrial increase | [8 empty] | 0 | 0
17 | Estimated peak hourly flow from future unidentified industries | [8 empty] | 0 | 0
18 | Peak hourly flow from other future increases | [8 empty] | 0 | 0
19 | Peak hourly wet weather design flow [(1)+(11)+(14)+(15)+(16)+(17)+(18)] | [5 empty] | = | 0 | Estimate | 0.249
(B) Determination of peak instantaneous wet weather design flow (PIWW): | [7 empty] | Gallons Per Day | Source
20 | Peak hourly wet weather design flow [same as (19)] | [6 empty] | 0 | Estimate | 0.249 | 249000
21 | Present peak hourly inflow adjusted for a 5-year 1-hour rainfall event [same as (8)] | [5 empty] | - | 0 | Estimate | 0.114
22 | Present peak inflow adjusted for a 25-year 1-hour rainfall event | [5 empty] | + |  | Estimate | 0.188 | 188000
23 | Peak instantaneous wet weather design flow | [5 empty] | = | 0 | Estimate | 0.323
(C) Determination of average dry weather design flow (ADW): | [7 empty] | Gallons Per Day | Source
24 | Present average dry weather flow | [7 empty] | DMR Data | 0.03 | 30000
25 | Population increase: |  | persons | @ |  | gpcd |  | 0 |  | 0
26 | Average flow from planned industrial increase | [5 empty] | + |  |  | 0 | 0
27 | Estimated average flow from other future unidentified industries | [5 empty] | + |  |  | 0 | 0
28 | Average flow from other future increases | [5 empty] | + |  |  | 0 | 0
29 | Average dry weather design flow [(24)+(25)+(26)+(27)+(28)] | [5 empty] | = | 0 |  | 0.03
(D) Determination of average wet weather design flow (AWW):
| (30 day average for mechanical plants, 180 day average for controlled discharge ponds) | [6 empty] | Gallons Per Day | Source
30 | Present average dry weather flow | [7 empty] | DMR Data | 0.03 | 30000
31 | Average infiltration after rehabilitation (where rehabilitation is cost effective) | [5 empty] | + |  | Estimate | 0.0226 | 22600
32 | Average inflow after rehabilitation (where rehabilitation is cost effective) | [5 empty] | + |  | Estimate | 0.0075 | 7500
33 | Population increase: |  | persons | @ |  | gpcd | + | 0 |  | 0
34 | Average flow from planned industrial increase | [5 empty] | + |  |  | 0 | 0
35 | Estimated average flow from other future unidentified industries | [5 empty] | + |  |  | 0 | 0
36 | Average flow from other future increases | [5 empty] | + |  |  | 0 | 0
37 | Average wet weather design flow [(30)+(31)+(32)+(33)+(34)+(35)+(36)] | [5 empty] | = | 0 | DMR Data | 0.0601
(E) Critical data (including a graphical display similar to Figure 1), methodology, and a discussion on the following items shall be included with the above calculations:
38 | Dates during which actual flow data was recorded and its probable degree of accuracy.
39 | Ground water elevation data relative to the collection system, during the time period when flow data was recorded.
40 | Rainfall data during the time period when flow data was recorded and how the amount of rainfall compares to normal seasons.
41 | Probable degree of accuracy of flow reduction due to proposed or completed I/I correction or elimination of bypasses.
Note on G24: gallons per capita per day
Note on G38: gallons per capita per day
Note on G49: gallons per capita per day

## Design Loadings - Table 3
Design loading determination worksheet
Project name | 0
Location | 0 |  |  |  |  | Intentionally Blank
Completed by | 0 |  |  |  |  | Input Cell - blue
Consultant | 0 |  |  |  |  | Calculation cell - no color
Date | 0
|  |  | Value | units | ADW | AWW
Residential waste |  | Population |  | people
|  | Flow, GPD/person |  | gpd/person | flow from table 3 (editable) | flow from table 3 (editable)
|  | Flow, GPD (total) | 0 |  | 0 | 0
|  | BOD5, #/day |  | mg/l | 0 | 0
|  | TSS, #/day |  | mg/l | 0 | 0
|  | NH3-N, #/day |  | mg/l | 0 | 0
|  | P, #/day |  | mg/l | 0 | 0
Out-of-town students and workers |  | Number |  | people
|  | Flow, GPD |  | gpd/person | 0 | 0
|  | BOD5, #/day |  | mg/l | 0 | 0
|  | TSS, #/day |  | mg/l | 0 | 0
|  | NH3-N, #/day |  | mg/l | 0 | 0
|  | P, #/day |  | mg/l | 0 | 0
Seasonal residents |  | Number |  | people
|  | Flow, GPD |  | gpd/person | 0 | 0
|  | BOD5, #/day |  | mg/l | 0 | 0
|  | TSS, #/day |  | mg/l | 0 | 0
|  | NH3-N, #/day |  | mg/l | 0 | 0
|  | P, #/day |  | mg/l | 0 | 0
Industrial |  | Flow, GPD |  | GPD
|  | Rated Flow, GPD |  | gpd/person | 0 | 0
|  | BOD5, #/day |  | mg/l | 0 | 0
|  | TSS, #/day |  | mg/l | 0 | 0
|  | NH3-N, #/day |  | mg/l | 0 | 0
|  | P, #/day |  | mg/l | 0 | 0
Other (Specify) |  | Flow, GPD |  | GPD
|  | Rated Flow, GPD |  | GPD | 0 | 0
|  | BOD5, #/day |  | mg/l | 0 | 0
|  | TSS, #/day |  | mg/l | 0 | 0
|  | NH3-N, #/day |  | mg/l | 0 | 0
|  | P, #/day |  | mg/l | 0 | 0
Infiltration (in addition to Table 2 amount, if applicable) |  | GPD
Inflow (in addition to Table 2 amount, if applicable) |  | GPD
Total |  | Flow, GPD |  |  | 0 | 0
|  | BOD5, mg/l |  |  | #DIV/0! | #DIV/0!
|  | BOD5, #/day |  |  | 0 | 0
|  | TSS, mg/l |  |  | #DIV/0! | #DIV/0!
|  | TSS, #/day |  |  | 0 | 0
|  | NH3-N, mg/l |  |  | #DIV/0! | #DIV/0!
|  | NH3-N, #/day |  |  | 0 | 0
|  | P, mg/l |  |  | #DIV/0! | #DIV/0!
|  | P, #/day |  |  | 0 | 0

## Summary Table 4
Design flow and loading summary table
| Project name | 0 |  |  |  |  | Text input - green
| Location | 0 |  |  |  |  | Number input - blue
| Completed by | 0 |  |  | Date | 0 | Calculation - no color
| Consultant | 0
Population
flow from table 2
| PHWW | 0 | gpd | 0 | mgd
| PIWW | 0 | gpd | 0 | mgd
| ADW | 0 | gpd | 0 | mgd
| AWW | 0 | gpd | 0 | mgd
mg/l based on AWW flow
| BOD |  | #/day | #DIV/0! | mg/l
| TSS |  | #/day | #DIV/0! | mg/l
| Phos |  | #/day | #DIV/0! | mg/l
| Nitrogen |  | #/day | #DIV/0! | mg/l
Others (list) |  |  | #/day | #DIV/0! | mg/l
Others (list) |  |  | #/day | #DIV/0! | mg/l
Others (list) |  |  | #/day | #DIV/0! | mg/l
Others (list) |  |  | #/day | #DIV/0! | mg/l
Others (list) |  |  | #/day | #DIV/0! | mg/l
Others (list) |  |  | #/day | #DIV/0! | mg/l
Others (list) |  |  | #/day | #DIV/0! | mg/l
Design flow and loading determination worksheets
Municipal/Industrial Wastewater
Doc Type: Engineering Report
wq-wwtp5-20a (Revised 2/3/23)