|  | Active Mitigation System Installation Checklist Remediation Program Vapor Intrusion/Mitigation Doc Type: Site Inspection Information |
| --- | --- |

## Instructions:  This checklist is to be completed by the contractor conducting installation of an active mitigation system as a building control for vapor mitigation. A copy of the completed checklist should be included in Appendix D of the Property Summary Report (PSR) which documents vapor mitigation activities completed for the property.

1.	General site and contractor information

| 1.1 | Site name: |  |
| --- | --- | --- |
| 1.2 | MPCA site ID number: |  |
| 1.3 | Property address: |  |
| 1.4 | Property owner name: |  |
| 1.5 | Property owner phone/email: |  |
| 1.6 | Date(s) of mitigation system installation (mm/dd/yyyy): |  |
| 1.7 | Installation contractor name: |  |
| 1.8 | Installation contractor phone/email: |  |

2.	System component considerations

|  |  | Yes | No | NA |
| --- | --- | --- | --- | --- |
| 2.1 | Is there evidence that contaminant type(s) and concentrations are present that warrant consideration of intrinsically safe system components? |  |  |  |
| 2.2 | If yes, has the system been constructed to be intrinsically safe? |  |  |  |
| 2.3 | Were the locations of all system components (suction points, fans, and system piping) approved by the property owner prior to installation? |  |  |  |
| 2.4 | Illustrate active mitigation system component locations on the floor plan in Section 9. |  |  |  |

3.	System installation and interior piping

|  |  | Yes | No | NA |
| --- | --- | --- | --- | --- |
| 3.1 | Are all suction point, manifold, exhaust piping and fittings solid, Schedule 40 pipe not less than 3 inches inside diameter? |  |  |  |
| 3.2 | Indicate the diameter of suction, manifold and exhaust pipes: 3 inch (suction/manifold/exhaust) 4 inch (suction/manifold/exhaust) 6 inch (suction/manifold/exhaust) 8 inch (suction/manifold/exhaust) |  |  |  |
|  | Other (list): |  |  |  |  |
| 3.3 | Are all pipe interior joints and connections in mitigation systems sealed permanently? (Exceptions include installation of fans and sump covers) |  |  |  |
| 3.4 | Does the system piping avoid attachment to or support by existing pipes, ducts, conduits or any kind of equipment? |  |  |  |
| 3.5 | Does the system piping avoid blocking window and doors or access to installed equipment? |  |  |  |
| 3.6 | Are supports for system piping installed at least every six (6) feet on horizontal runs? |  |  |  |
| 3.7 | Are vertical runs secured above or below the points of penetration through floors, ceilings and roofs, or at least every (8) feet on runs that do not penetrate floors, ceilings, or roofs? |  |  |  |
| 3.8 | Are suction point pipes supported and secured in a permanent manner that prevents their downward movement to the bottom of suction pits or sump pits, or into the soil beneath a soil-gas-retarder membrane? |  |  |  |
| 3.9 | Vent pipes are installed in a configuration that ensures that any rain water or condensation drains downward into the ground beneath the slab or soil gas retarder membrane? |  |  |  |
| 3.9 | Vent pipes are installed in a configuration that ensures that any rain water or condensation drains downward into the ground beneath the slab or soil gas retarder membrane? |  |  |  |
| 3.10 | Are fire collars installed around any piping that penetrates a firewall? |  |  |  |

4.	Fan installation information

| 4.1 | Total number of fans installed: |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.2 | Fan make and model: |  |  |  |  |
| 4.3 | Maximum wattage: |  |  |  |  |
| 4.4 | Fan manufacturer’s specifications for maximum CFM and pressure: |  |  |  |  |
| 4.5 | Indicate the locations of all installed mitigation system fans. Fans are to be installed in unconditioned spaces: Attic (unconditioned) Garage Outside 8 inch (suction/manifold/exhaust) |  |  |  |
|  | Other (specify): |  |  |  |  |
|  |  | Yes | No | NA |
| 4.6 | Is the fan installed in a vertical run of the vent pipe? |  |  |  |
| 4.7 | Is the fan mounted to the vent pipe with removable or flexible connections? |  |  |  |
| 4.8 | If the fan is mounted on the exterior of the building, is it rated for outdoor use or installed in a weather proof protective housing? |  |  |  |
| 4.9 | If the fan is mounted on the exterior of the building, is the fan and pipe run chased and insulated to prevent freezing in winter conditions? |  |  |  |
| 4.10 | Does the system operate without noise or vibration above normal conditions? |  |  |  |
| 4.11 | Is the total circuit load <80% of capacity (12 amps for 15 amp circuit, 16 for 20 amp circuit)? |  |  |  |
| 4.12 | Is the fan on a dedicated circuit if the load is >50% of capacity? |  |  |  |

5.	Monitors and labeling

|  |  | Yes | No | NA |
| --- | --- | --- | --- | --- |
| 5.1 | Is a manometer (or other approved indicator device) installed on at least one of the suction points of the mitigation system to allow for confirmation of system operation? |  |  |  |
| 5.2 | Is a system description label placed on the mitigation system? |  |  |  |
| 5.3 | Initial system differential pressure: |  | inches of water column |  |  |  |
|  | Date of initial differential pressure reading (mm/dd/yyyy): |  |  |  |  |
| 5.4 | Is the label legible from a distance of at least three feet and does it display the following information: Purpose of the system (Vapor Intrusion Mitigation), name and phone number of the contact person? |  |  |  |
| 5.5 | Are vent pipes labeled on each level where pipe is visible? |  |  |  |
| 5.6 | Is the circuit breaker controlling the circuit on which the vent fan operates labeled? |  |  |  |
| 5.7 | Is the current vacuum reading within 0.25” water of the initial reading for low vacuum fans and within 5% of the commissioned vacuum for high vacuum fans? |  |  |  |
| 5.8 | Was the system tested in the worst case scenario (e.g., all fans/dryers/vents, furnace/HVAC/ air exchangers) in operation? |  |  |  |
| 5.9 | Was a carbon monoxide (CO) detector installed or present and operable in the building after active system installation? |  |  |  |
| 5.10 | If yes, where is the carbon monoxide detector located: |  |  |  |  |

6.	System vent discharge

|  |  | Yes | No | NA |
| --- | --- | --- | --- | --- |
| 6.1 | Is the vent pipe vertical and upward, outside the structure, at least 10 feet above ground level, and above the edge of the roof? (Req. A) |  |  |  |
| 6.2 | Is the discharge of the vent pipe ten feet or more away from any window, door, or other opening into conditioned or otherwise occupiable spaces of the structure, if the vapor discharge point is not at least 2 feet above the top of such openings? (Req. B) |  |  |  |
| 6.3 | Is the discharge of the vent pipe ten feet or more away from any opening into the conditioned or other occupiable spaces of an adjacent building? Chimney flues shall be considered openings. (Req. C) |  |  |  |
| 6.4 | For vent stack pipes that penetrate the roof, is the point of discharge at least 12 in. above the surface of the roof? (Req. D) |  |  |  |
| 6.5 | For vent stack pipes attached to or penetrating the sides of the buildings, is the point of discharge vertical and a minimum of 12 inches above the surface of the roof? |  |  |  |
| 6.6 | Does the horizontal run of vent stack pipe penetrate the gable end walls? (Req. E) |  |  |  |
| 6.7 | If yes, is the piping outside the structure routed to a vertical position so that the discharge point meets the requirements of (A), (B), (C), and (D) listed above? |  |  |  |
| 6.8 | Do points of discharge that are not in a direct line of sight from openings into conditioned or otherwise occupiable space because of intervening objects, such as dormers, chimneys, windows around the corner, etc. meet the separation requirements of (A), (B), (C), (D) and (E)? |  |  |  |
| 6.9 | Is the outside vent piping fastened to the structure of the building with hangers, strapping or other supports that will secure it adequately (every 8 feet)? |  |  |  |
| 6.10 | Is vent stack piping’s inner diameter at least as large as the largest used in the manifold piping? |  |  |  |
| 6.11 | If system piping is installed on the exterior of a building, is piping and electric conduit sealed from the outside at point of entry into the building? |  |  |  |

7.	Sump pit

Provide written and verbal communication to the property owner and tenants for the requirement to keep the sump sealed and to re-seal in the event that the seal is broken during maintenance activities.

|  |  | Yes | No | NA |
| --- | --- | --- | --- | --- |
| 7.1 | Is there a sump pit present? |  |  |  |
| 7.2 | If yes, indicate number and location(s): |  |  |  |  |
| 7.3 | Is the sump pit cover constructed to facilitate removal for sump pump/pit maintenance? |  |  |  |
| 7.4 | Is the mitigation system constructed to draw soil-gas from the sump pit? |  |  |  |
| 7.5 | If yes, does the vent pipe have a disconnect for easy removal for sump pump maintenance? |  |  |  |

8.	Crawlspace sub-membrane depressurization system

|  |  | Yes | No | NA |
| --- | --- | --- | --- | --- |
| 8.1 | Was a sub-membrane depressurization system installed in a crawlspace area or area without a concrete floor as part of the mitigation system? |  |  |  |
| 8.2 | Is the vapor barrier membrane a minimum of 6 mil (3 mil cross-laminated) polyethylene? |  |  |  |
| 8.3 | Are the seams overlapped at least 12 inches and sealed using compatible materials? |  |  |  |
| 8.4 | Is the vapor barrier membrane secured to the wall using furring strips or appropriate sealants |  |  |  |
| 8.5 | Did the sub-membrane depressurization system pass the smoke test after installation? |  |  |  |

9.	Active mitigation system diagram

Include: suction points, fans, system manometer, sumps, crawl spaces, system piping, exhaust discharge, electrical panel.

| Scale: | North |  | (circle one) |
| --- | --- | --- | --- |

# Text boxes

Attachment B