|  | UST liquid sensor inspection form Underground Storage Tanks (UST) Program Doc Type: Compliance Certification |
| --- | --- |

Purpose:  This form is for documenting the inspection of the interstitial liquid sensors. See PEI/RP1200, Section 8 for inspection procedures.

## Facility information

| Facility name: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Facility address: |  |  |  |  |  |  |  |  |  |  | Facility ID#: |  |  |
| City: |  |  |  |  |  |  |  | State: |  |  |  | Zip code: |  |
| Owner name: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mailing address: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  | State: |  |  |  | Zip code: |  |
| Phone: |  |  |  |  |  | Fax: |  |  | Email: |  |  |  |  |

## Testing information

| 1. Product stored |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 2. Sensor type* |  |  |  |  |  |  |
| 2. Sensor location** | Tank Piping Dispenser DW sump or spill bucket | Tank Piping Dispenser DW sump or spill bucket | Tank Piping Dispenser DW sump or spill bucket | Tank Piping Dispenser DW sump or spill bucket | Tank Piping Dispenser DW sump or spill bucket | Tank Piping Dispenser DW sump or spill bucket |
| 3. Test liquid | Water Product | Water Product | Water Product | Water Product | Water Product | Water Product |
| 4. Is the ATG console clear of any active or recurring warnings or alarms regarding the sensor? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 5. If the sensor is in alarm indicate why. |  |  |  |  |  |  |
| 6. Is the sensor alarm circuit operational? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 7. Has the sensor been inspected and in good operational condition? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 8. When placed in the test liquid, does the sensor trigger an alarm? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 9. When an alarm is triggered, is the sensor properly identified on the ATG console? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 10. Is the sensor positioned properly? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 11. Is the sensor compatible with the fuel stored? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 12. When an alarm is triggered is the STP shut down? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| A “No” in lines 4 or 6-11 indicates a failure. |  |  |  |  |  |  |
| Test results: | Pass Fail | Pass Fail | Pass Fail | Pass Fail | Pass Fail | Pass Fail |

*Indicate if sensor is float switch, optical, electrical resistance, other (specify).

**Piping is STP or transition sump.

| Comments: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Testing company name: |  | Tester’s name: |  |  |
| Date (mm/dd/yyyy): |  |  | Tester’s signature: |  |