|  | UST overfill alarm inspection form Underground Storage Tanks (UST) Program Doc Type: Compliance Certification |
| --- | --- |

Purpose:  This form is for documenting the inspection of overfill alarms. See PEI/RP1200, Section 7 for inspection procedures.

## Facility information

| Facility name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Facility address: |  |  |  |  |  |  |  |  |  |  | Facility ID#: |  |  |  |
| City: |  |  |  |  |  |  |  | State: |  |  |  | Zip code: |  |  |
| Owner name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mailing address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  | State: |  |  |  | Zip code: |  |  |
| Phone: |  |  |  |  |  | Fax: |  |  | Email: |  |  |  |  |  |

Testing information

| 1. Tank number |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2. Product stored |  |  |  |  |  |  |  |  |  |
| 3. Tank volume, gallons |  |  |  |  |  |  |  |  |  |
| 4. Tank diameter, inches |  |  |  |  |  |  |  |  |  |
| 5. Overfill device brand |  |  |  |  |  |  |  |  |  |
| 6. Does overfill alarm activate in the test mode at the console? |  | Yes No | Yes No |  | Yes No | Yes No |  | Yes No | Yes No |
| 7. When activated, can the overfill alarm be heard or seen while delivering to the tank? |  | Yes No | Yes No |  | Yes No | Yes No |  | Yes No | Yes No |
| 8. After removing the probe from the tank, has it been inspected and any damaged or missing parts replaced? |  | Yes No | Yes No |  | Yes No | Yes No |  | Yes No | Yes No |
| 9. Float moves freely without binding? |  | Yes No | Yes No |  | Yes No | Yes No |  | Yes No | Yes No |
| 10. Does moving the product level up the shaft trigger the alarm? |  | Yes No | Yes No |  | Yes No | Yes No |  | Yes No | Yes No |
| 11. Inch level from bottom of shaft when 90% alarm is triggered. |  |  |  |  |  |  |  |  |  |
| 12. Tank volume at inch level in line 11. |  |  |  |  |  |  |  |  |  |
| 13. Calculate (line 12/ line 3) x 100 |  |  |  |  |  |  |  |  |  |
| 14. Is line 13 less than 90%? |  | Yes No | Yes No |  | Yes No | Yes No |  | Yes No | Yes No |
| 15. Does the fuel float level on the console agree with the gauge stick reading? |  | Yes No | Yes No |  | Yes No | Yes No |  | Yes No | Yes No |
| 16. Does the overfill alarm activate at any product level above 90% of tank capacity? |  | Yes No | Yes No |  | Yes No | Yes No |  | Yes No | Yes No |
| If any answers in lines 6-10 or 14 are “No” the system has failed the test. |  |  |  |  |  |  |  |  |  |
| Test results: |  | Pass Fail | Pass Fail |  | Pass Fail | Pass Fail |  | Pass Fail | Pass Fail |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |
| Testing company name: |  |  |  |  | Tester’s name: |  |  |  |  |  |
| Date (mm/dd/yyyy): |  |  |  |  | Tester’s signature: |  |  |  |  |  |