|  | UST overfill equipment inspection form Underground Storage Tanks (UST) Program Doc Type: Compliance Certification |
| --- | --- |

Purpose:  This form is for documenting the inspection of automatic shutoff devices and ball float valves. See PEI/RP1200, Section 7 for inspection procedures.

## Facility information

| Facility name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Facility address: |  |  |  |  |  |  |  |  |  |  | Facility ID#: |  |  |  |
| City: |  |  |  |  |  |  |  | State: |  |  |  | Zip code: |  |  |
| Owner name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mailing address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  | State: |  |  |  | Zip code: |  |  |
| Phone: |  |  |  |  |  | Fax: |  |  | Email: |  |  |  |  |  |

Testing information

| 1. Tank number |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 2. Product stored |  |  |  |  |  |  |
| 3. Tank volume, gallons |  |  |  |  |  |  |
| 4. Tank diameter, inches |  |  |  |  |  |  |
| 5. Overfill device brand |  |  |  |  |  |  |
| 6. Type | Auto shutoff Ball float | Auto shutoff Ball float | Auto shutoff Ball float | Auto shutoff Ball float | Auto shutoff Ball float | Auto shutoff Ball float |
| Automatic shutoff inspection |  |  |  |  |  |  |
| 7. Drop tube removed from the tank? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 8. Drop tube and float are free of debris? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 9. Float moves freely without binding and poppet moves into flow path? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 10. Bypass valve is open and free of blockage (if present)? | Yes No NA | Yes No NA | Yes No NA | Yes No NA | Yes No NA | Yes No NA |
| 11. Flapper is adjusted to shut off flow at 95% capacity? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| A “No” in any line 7-11 indicates a failure |  |  |  |  |  |  |
| Ball float valve inspection |  |  |  |  |  |  |
| 12. Tank top fittings are vapor tight and leak-free? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 13. Ball float cage free of debris? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 14. Ball is free of holes and cracks and moves freely in cage? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 15. Vent hole in pipe is open and near top of tank? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| 16. Ball float pipe is proper length to restrict flow at 90% capacity? ** | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No |
| A “No” in any line 12-16 indicates a failure |  |  |  |  |  |  |
| Test results: | Pass Fail | Pass Fail | Pass Fail | Pass Fail | Pass Fail | Pass Fail |

*Use manufacturer’s suggested procedure for determining if auto shutoff device will shut off flow at 95% capacity.

** Use manufacturer’s suggested procedure for determining if flow restriction device will restrict flow at 90% capacity.

| Comments: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Testing company name: |  | Tester’s name: |  |  |
| Date (mm/dd/yyyy): |  |  | Tester’s signature: |  |