|  | UST emergency stop switch inspection form Underground Storage Tanks (UST) Program Doc Type: Compliance Certification |
| --- | --- |

Purpose:  This form is to verify the operation of all emergency stop switches/buttons (E-stop). Each E-stop must disconnect power to dispensers, submersible turbine pumps (STP’s) and all non-intrinsically safe electrical equipment in classified areas. Test each E-stop seperately. See PEI/RP1200, Section 11 for inspection procedure.

## Facility information

| Facility name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Facility address: |  |  |  |  |  |  |  |  |  |  | Facility ID#: |  |  |  |
| City: |  |  |  |  |  |  |  | State: |  |  |  | Zip code: |  |  |
| Owner name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mailing address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  | State: |  |  |  | Zip code: |  |  |
| Phone: |  |  |  |  |  | Fax: |  |  | Email: |  |  |  |  |  |

Testing information

| 1. E-stop number or ID |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2. Location |  |  |  |  |  |  |  |  |  |  |
| 3. System is fully powered and in normal operating condition? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| 4. After activating E-stop, power has been disconnected from: |  |  |  |  |  |  |  |  |  |  |
| 4a. All dispensing devices on all islands? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| 4b. All STPs for all grades of fuel? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| 4c. All power, control and signal circuits associated with the dispensing devices and the STPs? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| 4d. All other non-intrinsically safe electrical equipment in classified areas surrounding fuel dispensing devices? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| 5. Are the E-stops properly located within 100 feet of the dispensers but not closer than 20 feet from the dispensers? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| 6. Are the E-stops clearly identified? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| 7. All intrinsically safe electrical equipment remains energized after E-stop activation? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| 8. After testing, has E-stop been reset and power reestablished to normal operating condition? |  |  | Yes No |  |  | Yes No | Yes No |  | Yes No | Yes No |
| A “No” to lines 6-11 indicates a test failure. |  |  |  |  |  |  |  |  |  |  |
| Test results: |  |  | Pass Fail |  |  | Pass Fail | Pass Fail |  | Pass Fail | Pass Fail |
| Comments: |  |  |  |  |  |  |  |  |  |  |
| Testing company name: |  |  | Tester’s name: |  |  |  |  |  |  |  |  |
| Date (mm/dd/yyyy): |  |  |  | Tester’s signature: |  |  |  |  |  |  |  |