|  | SOP 3.02 Storing Wastes for Greater than 90 Days - Information for HHW Programs |
| --- | --- |

Note: This guidance document is for informational purposes only and outlines basic employer requirements. The MPCA does not guarantee that this document satisfies OSHA and RCRA compliance; it is the sole responsibility of county-specific Household Hazardous Waste (HHW) Program employer to determine if all requirements have been met.

# 1.	Introduction

Prior to accepting HHW from another HHW facility, or storing HHW onsite for more than 90 days, this Program must obtain written approval from the State at least 30 days in advance. The HHW Program license may permit the acceptance of waste from other counties as specified by state requirements. This Facility shall also develop, maintain, and implement an Emergency Contingency Plan and SOPs specific to this Program. The designated staff person to implement this HHW SOP is [________________________].

# 2.	Greater-Than-90-Day Site Standards

2.1 	Construction and Storage Specifications

Program staff shall ensure that this HHW Facility meets the following standards:

- Located more than 150 feet from any water supply well.

- Maintains restricted access to prevent unauthorized entry.

- Provides receiving, sorting, packaging, and storage areas with impermeable flooring coated with chemically resistant epoxy.

- Contains no floor drains that lead to a sewer system or the environment within waste processing areas.

- Stores ignitable wastes in buildings located at least 50 feet from the property line, unless a written waiver is obtained from the local fire marshal and/or building officials.

- Complies with local zoning, building codes, fire codes, and OSHA requirements, including:

    - Explosion-proof equipment

    - Proper wiring and HVAC systems in fuel bulking area

    - Fire suppression equipment

    - Grounding and bonding of containers in fuel processing and storage areas

- Provides adequate ventilation to ensure safe air quality and fire prevention, with a minimum rate of 1 cubic foot per minute per square foot of floor space for Class I liquids or liquids with a flashpoint between 0°F and 100°F when bulked indoors.

- Ensures sufficient storage space so that all HW containers remain fully visible for inspections (labels, markings, condition, and potential spillage).

- Segregates containers of incompatible liquids using secondary containment (e.g., dikes, berms, curbs, walls) or maintains a minimum 10-foot separation.

- Grounds containers storing ignitable wastes.

- Stores ignitable waste under overhead roofing or protective covering that allows label visibility and prevents public access.

- Protects wastes susceptible to freezing to maintain container integrity and prevent spills.

Acceptance and collection of HHW are part of a county’s overall Solid Waste (SW) Management Program. The purpose of this program is to divert the hazardous portion of household waste from the SW, to prevent releases from SW facilities to the environment through leachate, as well as protect staff from hazardous or dangerous situations. Each county is required in section 115A.46 to include in its SW management plan a broad-based public education component. Several other statutes apply to collectors and household generators of wastes and products that contain hazardous constituents, including disposal bans.

2.2 	Equipment Requirements

The Facility shall incorporate and maintain the following equipment in proper working condition:

- Fire extinguishers with required signage and/or functional fire suppression systems with adequate volume and pressure.

- Clearly visible signage in Product Reuse area, including:

- “No Smoking”

- “Authorized Personnel Only”

- “No One Under the Age of 18 Allowed in Facility Without Adult Supervision”

- PaintCare

- Internal and external telephone or communication systems.

- Clearly labeled and stocked first-aid kits and spill response kits.

- Decontamination equipment, including an emergency eyewash and shower capable of providing

- 15 minutes of continuous water and located within a 10-second travel distance of areas where corrosive chemicals are handled.

- Facility ADA compliant doors and access to hand-washing facilities.

- A designated area for eating and drinking, supplied with potable water, and isolated from exposure to toxic materials.

- Ensure all containers storing HHW are clearly marked with the contents, the accumulation start date and the words ‘Hazardous Waste’.

- Publicly posted outdoor signage listing hours of operation, contact information, and a statement prohibiting unattended waste drop-off.