## Basin Information
Basin Information |  |  |  |  | = Enterable Cells
Basin Top Length | 150 | ft
Basin Top Width | 350 | ft
Basin Depth | 12 | ft
Side Wall Slope | 3 | :1
Free Board | 1 | ft
Sludge / Unpumpable | 1 | ft
Basin Average
Basin Bottom
Liner Thickness | 2 | ft
Average K | 1e-07 | cm/sec | FALSE
Basin Sidewalls
Liner Thickness | 2 | ft
Average K | 1.05e-07 | cm/sec
RESULTS
Basin Seepage
Basin Bottom Seepage (at Design HWL) |  | 600.346 |  | gal/acre-day
|  | 45.2279 |  | in/day
Basin Sidewall Seepage (at Design HWL) |  | 321.5944 |  | gal/acre-day
|  | 84.4306 |  | in/day
Basin Seepage is | Non-Compliant
NOTE: Both bottom and sidewall must be less than or equal to 1/56 inch/day
Basin Volume
Basin Overall Volume (at Design HWL) |  | 383724 |  | ft3
|  | 2870255.52 |  | gals
Basin Available Volume (at Design HWL Less Unpumpable) |  | 360960 |  | ft3
|  | 2699980.8 |  | gals
Convert in/day to gal/day on a per acre basis
Bottom Seepage Velocity (ft/day)
| 0.018425 | ft/day
k = permeability (ft/day)
i = hydraulic gradient
ne = effective porosity (0.10 for clay)
input separate values for both sidewalls and bottom

## Seepage Rate (hidden)
Seepage from Basin Estimate
Top Length | 150 | Top Width | 350 | Slope | 3 | :1
Liner Thickness | 2 | Design HWL | 11 | Depth | 12
Average K | 1e-07 | cm/sec
Average K | 0.00028346 | ft/day
Basin Bottom Summary - See Individual Sheet For Further Details
Total Flow | 39.9532 | cu ft/day
| 298.8499 | gal/day
Total Area | 21684 | sq ft
| 0.4978 | acres
Basin Side Slope Summary - See Individual Sheet For Further Details
Total Flow | 28.977 | cu ft/day
| 216.7483 | gal/day
Total Area | 29358.5858 | sq ft
| 0.67398 | acres
Overall Summary - Used for Compliance Determinations
Total Flow | 68.9302 | cu ft/day
| 515.5982 | gal/day
Total Area | 51042.5858 | sq ft
| 1.1718 | acres
Seepage Rate | 440.0141 | gal/acre-day

## Bottom Seepage
Seepage from Basin Estimate
Top Length | 150 | Top Width | 350 | Slope | 3 | :1
Liner Thickness | 2 | Design HWL | 11 | Depth | 12
Bottom Length | 78 | Bottom Width | 278
|  | i | 6.5
Basin Bottom
Bottom Area | 21684 | sq ft
Average K | 1e-07 | cm/sec
Average K | 0.00028346 | ft/day
Flow (Q) | 39.9532 | cu ft/day
Summary of Basin Bottom
Total Flow | 39.9532 | cu ft/day
| 298.8499 | gal/day
Total Area | 21684 | sq ft
| 0.4978 | acres
Seepage Rate | 600.346 | gal/acre-day

## Side Slope Seepage
Seepage from Basin Estimate | [7 empty] | Summary of Basin Side Slopes
Top Length | 150 | Top Width | 350 |  |  |  |  | Total Flow @ Design HWL | 28.977 | cu ft/day
Bottom Length | 78 | Bottom Width | 278 | [5 empty] | 216.7483 | gal/day
Design HWL | 11 | Depth | 12
Liner Thickness | 2 | Slope | 3 | :1 |  |  |  | Total Area @ Design HWL | 29358.5858 | sq ft
Average K | 1e-07 | cm/sec | [6 empty] | 0.67398 | acres
Average K | 0.00028346 | ft/day
[8 empty] | Seepage Rate | 321.5944 | gal/acre-day
Basin Side Slopes
Liquid Depth | i | Slope Length | Length at Liquid Depth |  | Width at Liquid Depth | Area Along Length | Area Along Width | Area of All Corners | Total Area | Seepage of Total Area
0 | 6.5 | 0 | 78 |  | 278 | 0 | 0 | 0 | 0 | 0
0.5 | 6.25 | 1.5811 | 81 |  | 281 | 246.6577 | 879.1132 | 9.4868 | 1135.2577 | 2.0113
1 | 6 | 1.5811 | 84 |  | 284 | 256.1445 | 888.6 | 9.4868 | 1154.2313 | 1.9631
1.5 | 5.75 | 1.5811 | 87 |  | 287 | 265.6313 | 898.0869 | 9.4868 | 1173.205 | 1.9122
2 | 5.5 | 1.5811 | 90 |  | 290 | 275.1182 | 907.5737 | 9.4868 | 1192.1787 | 1.8587
2.5 | 5.25 | 1.5811 | 93 |  | 293 | 284.605 | 917.0605 | 9.4868 | 1211.1523 | 1.8024
3 | 5 | 1.5811 | 96 |  | 296 | 294.0918 | 926.5474 | 9.4868 | 1230.126 | 1.7435
3.5 | 4.75 | 1.5811 | 99 |  | 299 | 303.5787 | 936.0342 | 9.4868 | 1249.0997 | 1.6819
4 | 4.5 | 1.5811 | 102 |  | 302 | 313.0655 | 945.521 | 9.4868 | 1268.0733 | 1.6175
4.5 | 4.25 | 1.5811 | 105 |  | 305 | 322.5523 | 955.0079 | 9.4868 | 1287.047 | 1.5505
5 | 4 | 1.5811 | 108 |  | 308 | 332.0392 | 964.4947 | 9.4868 | 1306.0207 | 1.4808
5.5 | 3.75 | 1.5811 | 111 |  | 311 | 341.526 | 973.9815 | 9.4868 | 1324.9943 | 1.4085
6 | 3.5 | 1.5811 | 114 |  | 314 | 351.0128 | 983.4684 | 9.4868 | 1343.968 | 1.3334
6.5 | 3.25 | 1.5811 | 117 |  | 317 | 360.4997 | 992.9552 | 9.4868 | 1362.9417 | 1.2556
7 | 3 | 1.5811 | 120 |  | 320 | 369.9865 | 1002.442 | 9.4868 | 1381.9153 | 1.1752
7.5 | 2.75 | 1.5811 | 123 |  | 323 | 379.4733 | 1011.9289 | 9.4868 | 1400.889 | 1.092
8 | 2.5 | 1.5811 | 126 |  | 326 | 388.9602 | 1021.4157 | 9.4868 | 1419.8627 | 1.0062
8.5 | 2.25 | 1.5811 | 129 |  | 329 | 398.447 | 1030.9025 | 9.4868 | 1438.8363 | 0.91768
9 | 2 | 1.5811 | 132 |  | 332 | 407.9338 | 1040.3894 | 9.4868 | 1457.81 | 0.82647
9.5 | 1.75 | 1.5811 | 135 |  | 335 | 417.4207 | 1049.8762 | 9.4868 | 1476.7837 | 0.73258
10 | 1.5 | 1.5811 | 138 |  | 338 | 426.9075 | 1059.363 | 9.4868 | 1495.7573 | 0.63599
10.5 | 1.25 | 1.5811 | 141 |  | 341 | 436.3943 | 1068.8498 | 9.4868 | 1514.731 | 0.53672
11 | 1 | 1.5811 | 144 |  | 344 | 445.8812 | 1078.3367 | 9.4868 | 1533.7047 | 0.43475
11.5 | 0.75 | 1.5811 | 147 |  | 347 | 455.368 | 1087.8235 | 9.4868 | 1552.6783 | 0.3301
12 | 0.5 | 1.5811 | 150 |  | 350 | 464.8548 | 1097.3103 | 9.4868 | 1571.652 | 0.22275

## Basin Volume
Basin Volume
Top Length | 150 | ft |  | Design HWL Volume
Top Width | 350 | ft |  | 383724 | cu ft
Slope | 3 | :1 |  | 2870255.52 | gals
Depth | 12 | ft
Free Board | 1 | ft |  | Design Available Volume
Sludge | 1 | ft |  | 360960 | cu ft
Design HWL | 11 | ft |  | 2699980.8 | gals
Liquid Depth | Length |  | Width | Volume (ft3) | Volume (gals)
0 | 78 |  | 278 | 0 | 0
0.5 | 81 |  | 281 | 11110.5 | 83106.54
1 | 84 |  | 284 | 22764 | 170274.72
1.5 | 87 |  | 287 | 34969.5 | 261571.86
2 | 90 |  | 290 | 47736 | 357065.28
2.5 | 93 |  | 293 | 61072.5 | 456822.3
3 | 96 |  | 296 | 74988 | 560910.24
3.5 | 99 |  | 299 | 89491.5 | 669396.42
4 | 102 |  | 302 | 104592 | 782348.16
4.5 | 105 |  | 305 | 120298.5 | 899832.78
5 | 108 |  | 308 | 136620 | 1021917.6
5.5 | 111 |  | 311 | 153565.5 | 1148669.94
6 | 114 |  | 314 | 171144 | 1280157.12
6.5 | 117 |  | 317 | 189364.5 | 1416446.46
7 | 120 |  | 320 | 208236 | 1557605.28
7.5 | 123 |  | 323 | 227767.5 | 1703700.9
8 | 126 |  | 326 | 247968 | 1854800.64
8.5 | 129 |  | 329 | 268846.5 | 2010971.82
9 | 132 |  | 332 | 290412 | 2172281.76
9.5 | 135 |  | 335 | 312673.5 | 2338797.78
10 | 138 |  | 338 | 335640 | 2510587.2
10.5 | 141 |  | 341 | 359320.5 | 2687717.34
11 | 144 |  | 344 | 383724 | 2870255.52
11.5 | 147 |  | 347 | 408859.5 | 3058269.06
12 | 150 |  | 350 | 434736 | 3251825.28

## Diff. Slope Basin Volume
Volume of a basin with various sidewall slopes
|  | TL | Top Length | 492
|  | TW | Top Width | 90
|  | S1 | Slope Side 1 | 3
|  | S2 | Slope Side 2 | 3
|  | S3 | Slope Side 3 | 3
|  | S4 | Slope Side 4 | 10
|  | FB | Free Board | 4
|  | D | Total Basin Depth | 11
|  | BL | Bottom Length | 349
|  | BW | Bottom Width | 24
Total Basin Volume | Volume at Design HWL
272305 | 126497
TL
TW
BL
BW
S3
S2
S1
S4

## Combining Permeability
Calculate the overall permeability of two layers with different permeability test results
Lower (base) material
Thickness of material (in) | H1 | 12 | inches
Permeability of material (cm/sec) | k1 | 2.5e-07 | cm/sec
Upper (top) material
Thickness of material (in) | H2 | 12 | inches
Permeability of material (cm/sec) | k2 | 8.2e-08 | cm/sec
3rd material layer (optional)
Thickness of material (in) | H3 |  | inches
Permeability of material (cm/sec) | k3 |  | cm/sec
Combined Permeability | Kfinal | 1.2349e-07 | cm/sec
H2
H1