## Performance
NPDES Number | Facility Name | State (select from dropdown) | Baseline Treatment System Description | Nutrient Removal Project Description and [Target Nutrient(s)] | Upgraded Treatment System Type and Retrofit or Replace for Cost Estimation Purposes (select from dropdown) | Average Flow (MGD) | Design Flow (MGD) | Average Flow as a % of Design Flow | Average Monthly Influent TN (as N) Concentration | Post-Project Average Monthly Effluent TN (as N) Concentration | Post-Project Average TN % Removal (Concentration) (calculated) | Pre-Project Average Monthly Effluent TN (as N) Concentration | Period of Record for TN (as N) Influent Concentration | Period of Record for Post-Project TN (as N) Effluent Concentration | Period of Record for Pre-Project TN (as N) Effluent Concentration | Notes
IA0029025 | City of Atlantic WWTP | Iowa | Trickling Filters | BNR [Total Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 7.7 | 8.1 | 95.06% | 33.06 | 4.35 | 86.84% | 21 | 11/2019 - 7/2024 | 12/2016 - 6/2024 | Estimated | Assumed BNR 3- to 5-stage replace based on description; conservatively assumed 100% of upgrade capital cost attributed to nutrient removal; no O&M cost reported
MN0020192 | Detroit Lakes WRF | Minnesota | Trickling Filters | Membrane Bioreactor with Bio-P [Phosphorus] | NA | 1.08 | 2.21 | 48.87% | 40.55 | 8.89 | 78.08% | 24.82 | 10/2019 - 8/2024 | 9/2019 - 8/2024 | 11/2017 - 6/2019 | Upgraded system includes MBR; total capital cost of upgrades provided by facility; percent of capital cost attributed to nutrient removal project estimated based on conservative estimate from CapdetWorks cost model; pre-project O&M cost and % of upgrade O&M cost attributed to nutrient removal project based on estimates from CapdetWorks cost model using post-upgrade O&M cost provided by facility
MN0030066 | New Ulm WWTP | Minnesota | Activated Sludge + Biological Phosphorus Removal | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 2.3 | 6.77 | 33.97% | 32.04 | 10.38 | 67.6% | 21 | 9/2019 - 7/2024 | 3/2015 - 7/2024 | Estimated | Assumed "BNR 2-Stage Replace" based on reported addition of tanks; entire capital cost of upgrade reported by facility is attributed to nutrient removal; no O&M cost reported by facility
MN0040878 | St. Cloud NEW RF | Minnesota | Conventional Step-Feed Activated Sludge | Full Nitrification and BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 9.88 | 17.9 | 55.2% | 47.02 | 13.8 | 70.65% | 21 | 9/2019 - 7/2024 | 5/2017 - 7/2024 | Estimated | Assumed "BNR 3- to 5-Stage Retrofit" based on report of modifications made to existing plant; capital cost reported by facility for BNR and additional secondary clarifiers; 100% of this cost attributed to nutrient removal; no O&M cost reported by facility
MN0066079 | City of Long Prairie WWTF | Minnesota | Conventional Activated Sludge | Extended Aeration Activated Sludge/BNR [Phosphorus] | A/O or BNR 2-Stage Replace | 1.26 | 2.279 | 55.29% | 66.44 | 18.06 | 72.82% | 45.21 | 9/2019 - 7/2024 | 1/2020 - 6/2024 | 6/2018 - 12/2019 | Assumed "BNR 2-Stage Replace" based on reported construction of new aeration basins; some basins converted to anoxic basins; 100% of capital cost attributed to nutrient removal; no O&M cost reported by facility
MT0020125 | Chinook WWTF | Montana | Activiated Sludge-Oxidation Ditch | Activated Sludge-Oxidation Ditch; Optimized through mixers, DO probe, and SCADA [Nitrogen] | NA | 0.055 | 0.5 | 11% | 40 | 2.82 | 92.95% | 21 | Estimated | 7/2014 - 8/2024 | Estimated | No major infrastructure changes; addition of mixers, DO probe, and SCADA; negative O&M cost based on reported energy cost savings (before and after installation of new equipment)
MT0021938 | City of Kalispell Advanced Wastewater Treatment and Biological Nutrient Removal Facility | Montana | Modified University of Capetown | Modified Johannesburg BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 2.85 | 5.4 | 52.78% | 40 | 7.82 | 80.45% | 21 | Estimated | 7/2014 - 8/2024 | Estimated | Capital cost provided by facility for conversion of Modified UCT to Johannesburg and for expansion of faclity capacity (characterized here as BNR 3- to 5-stage retrofit; assumed no additional O&M cost based on facility estimate
MT0022594 | Missoula WWTP | Montana | Conventional Activated Sludge | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 6.9 | 12 | 57.5% | 40 | 9.63 | 75.92% | 21 | Estimated | 7/2014 - 8/2024 | Estimated | Assumed BNR 3- to 5-stage replace; capital cost provided by facility for upgrade of existing activated sludge system to BNR and addition of new BNR treatment units; no O&M cost information provided by facility
NY0027561 | LeRoy R Summerson WWTF (City of Cortland) | New York | Conventional Activated Sludge | Cycling Air and Adding Internal Carbon Source [Phosphorus, Nitrogen] | NA | 5.46 | 9 | 60.67% | 18.25 | 8.26 | 54.74% | 16.08 | 9/2019 - 7/2024 | 10/2022 - 7/2024 | 9/2014 - 9/2022 | There were no infrastructure changes at the facility; the faciltiy has been able to achieve consistently greater nutrient removal through reprogramming the SCADA system to cycle air in and off in the tanks and selectively bypassing the gravity clarifier to increase carbon to the tanks
IL0028053 | Stickney WRP | Illinois | Conventional Activated Sludge with EBPR | Ostara Phosphorus Recovery [Phosphorus] | A/O or BNR 2-Stage Retrofit | 679 | 1440 | 47.15% | 40 | 9.46 | 76.35% | 8.2 | Estimated | 1/2019 - 7/2024 | 7/2014 - 12/2018 | Plant appears to be optimized for phosphorus removal/recovery; effluent TN concentrations have increased since the nutrient recovery technology was brought online in 2019; however, concentrations remain below 10 mg/L
MN0020567 | Monticello WWTP | Minnesota | Conventional Activated Sludge | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 1.15 | 2.36 | 48.73% | 67.48 | 8.71 | 87.09% | 21 | 6/2020 - 8/2024 | 6/2020 - 8/2024 | Estimated | Assumed BNR 3- to 5-stage retrofit based on description; no information on cost or year of upgrade and no O&M cost information provided by facility
MN0055361 | Plainview Township WWTP | Minnesota | Conventional Activated Sludge | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 0.755 | 2.67 | 28.28% | 36.22 | 10.91 | 69.88% | 21 | 12/2022 - 8/2024 | 12/2022 - 8/2024 | Estimated | Assumed BNR 2-stage retrofit based on description of modification to biological phosphorus removal; minimum capital costs and no O&M cost provided by the facility; dry weather average flow of 1.92 MGD reported in project fact sheet is significantly greater than average monthly flow reported in DMRs
MT0022568 | Billings WRF | Montana | Complete Mix Activated Sludge | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 19.7 | 26 | 75.77% | 40 | 6.87 | 82.83% | 17.58 | Estimated | 7/2018 - 8/2024 | 7/2014 - 6/2018 | Assume BNR 3- to 5-stage replace; upgrade included both retrofitting and building new infrastructure; construction began in 2017; estimated pre- and post-project dates based on assumed construction time and break in effluent concentration data; no O&M cost provided by the facility
MT0022608 | Bozeman WRF | Montana | Complete Mix Activated Sludge | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 5.96 | 8.5 | 70.12% | 40 | 6.14 | 84.65% | 17.8 | Estimated | 7/2014 - 7/2024 | Estimated | Assume BNR 3- to 5-Stage replace based on a combination of 2007 upgrades to conventional activated sludge system to BNR in 2007 and addition of new 5-stage Bardenpho reactor in 2012; pre-2007 annual average reported by facility was 17.8 mg/L TN; post-2007/pre-2012 upgrade annual average reported by facility was 10.5 mg/L; estimated percent of capital cost attributed to upgrade based on approximate percentage of total treatment system cost attributed to nutrient removal treatment technology by cost model; assumes upgrade of all treatment units to increase capacity and performance and, therefore, only a percentage of total capital cost attributed to nutrient removal; no O&M cost provided by facility
MT0020435 | Livingston WRF | Montana | Rotating biological contactor | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 0.73 | 0.913 | 79.96% | 40 | 3.08 | 92.3% | 27.54 | Estimated | 8/2019 - 8/2024 | 7/2014 - 10/2018 | Design flow estimated based on actual average flow (average flow = 80% of design flow); assumed upgrade can be categorized as BNR 3- 5-stage replace based on replacement of RBCs with SBRs for phosphorus and nitrogen removal; total capital cost of upgrades provided by facility; percent of capital cost attributed to nutrient removal project estimated based on conservative estimate from CapdetWorks model; O&M cost estimate consistent with facility estimate of $1 million total O&M cost and CapdetWorks cost model estimate of 3.75% of the total O&M cost attributable to the nutrient removal technology
MT0020079 | Conrad WWTF | Montana | Lagoons | Extended Aeration Activated Sludge [Phosphorus] | A/O or BNR 2-Stage Replace | 0.191 | 0.5 | 38.2% | 40 | 6.5 | 83.75% | 21 | Estimated | 9/2014 - 8/2024 | Estimated | Assumed 2-Stage BNR replace based on description of upgrade from lagoons to extended aeration activated sludge. Total capital cost of upgrade from lagoons to activated sludge provided by facility; percent of capital cost attributed to nutrient removal project estimated as 25% of total cost; no O&M cost information provided by the facility.O&M cost estimate at design flow of 0.5 MGD, which is the lowest cost used in the model
MN0050725 | Kasson WWTP | Minnesota | Conventional Activated Sludge | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 0.812 | 2.07 | 39.23% | 39.04 | 10.1 | 74.13% | 21 | 10/2019 - 8/2024 | 3/2018 - 8/2024 | Estimated | Facility was upgraded in 2015 to regionalize wastewater treatment and serve Kasson and Mantorville. An aging oxidation ditch aerator was replaced and nutrient removal was enhanced by adding an MLSS recycle loop and upgrading system controls and instrumentation. No capital cost information was provided by the facility; cost estimates based on model estimates for adding 2-Stage BNR. Facility indicates that 2015 upgrades were estimated to save $17,000 in annual electricity costs.
WI0020478 | City of Sun Prairie WWTP | Wisconsin | Conventional Activated Sludge | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 3.53 | 7.53 | 46.88% | 40 | 16.98 | 57.55% | 21 | Estimated | 11/2018 - 6/2024 | Estimated | Effluent TN concentration data in DMRs are quarterly maximums, which would overestimate monthly average concentrations; few details on upgrade and no capital or O&M cost information; assumed 2-Stage BNR retrofit for biological phosphorus removal
MN0020117 | Central Iron Range Sanitary District WWTF | Minnesota | Conventional Activated Sludge | Sequencing Batch Reactors [Phosphorus] | A/O or BNR 2-Stage Replace | 0.8 | 2.5 | 32% | 28.77 | 6.76 | 76.5% | 21 | 2/2022 - 8/2024 | 2/2022 - 8/2024 | Estimated | Assumed reported average dry weather flow of 2.5 MGD is the design flow; average monthly flow reported in DMRs = 0.8 MGD; assumed upgrade can be categorized as BNR 2-stage replace based on upgrade to SBRs; no capital or O&M cost provided by facility
PA0080314 | Hampden Township WWTP | Pennsylvania | Continuously Sequencing Reactor | Added Process Control System [Nitrogen] | NA | 3.354 | 5.69 | 58.95% | 40 | 4.39 | 89.03% | 21 | Estimated | 7/2014 - 7/2024 | Estimated | 2010 upgrade consisted of addition of a process control system to monitor DO and nitrate; all available TN data are from after 2010; no capital or O&M cost provided by facility; assumed no cost attributed to nutrient removal (potentially O&M savings)
MA0100153 | Town of Lee WWTF | Massachusetts | Conventional Activated Sludge | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 0.726 | 1.5 | 48.4% | 40 | 3.75 | 90.62% | 21 | Estimated | 7/2014 - 3/2023 | Estimated | Assumed upgrade can be categorized as BNR 3- 5-stage replace based on replacement of conventional activated sludge with SBRs for phosphorus and nitrogen removal; total capital cost of upgrades provided by facility; percent of capital cost attributed to nutrient removal project estimated based on estimate from CapdetWorks model; no O&M cost provided by facility

## Loading Actual Flow
NPDES Number | Facility Name | Nutrient Removal Project and [Target Nutrient(s)] | Upgraded Treatment System Type and Retrofit or Replace for Cost Estimation Purposes (select from dropdown) | Average Flow (MGD) | Average Daily Influent TN (as N) Loading | Average Daily Effluent TN (as N) Loading Post-Project | Average lbs/day TN (as N) Removed Post-Project | Average Annual TN (as N) Removed (lbs) Post-Project | Average Daily Effluent TN (as N) Loading Pre-Project | Average lbs/day TN (as N) Removed Pre- Project | Average Annual TN (as N) Removed Pre- Project (lbs) Pre-Project | Average Annual TN (as N) Removed as a Result of Nutrient Removal Project based on Actual Flow
IA0029025 | City of Atlantic WWTP | BNR [Total Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 7.7 | 2123.0471 | 279.3483 | 1843.6988 | 672950.0547 | 1348.578 | 774.4691 | 282681.2142 | 390268.8405
MN0020192 | Detroit Lakes WRF | Membrane Bioreactor with Bio-P [Phosphorus] | NA | 1.08 | 365.242 | 80.074 | 285.168 | 104086.3025 | 223.5587 | 141.6833 | 51714.3884 | 52371.914
MN0030066 | New Ulm WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 2.3 | 614.5913 | 199.1092 | 415.4821 | 151650.9738 | 402.822 | 211.7693 | 77295.7872 | 74355.1866
MN0040878 | St. Cloud NEW RF | Full Nitrification and BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 9.88 | 3874.4104 | 1137.109 | 2737.3014 | 999115.0198 | 1730.3832 | 2144.0272 | 782569.9222 | 216545.0976
MN0066079 | City of Long Prairie WWTF | Extended Aeration Activated Sludge/BNR [Phosphorus] | A/O or BNR 2-Stage Replace | 1.26 | 698.1781 | 189.7817 | 508.3964 | 185564.6831 | 475.0848 | 223.0933 | 81429.0662 | 104135.6169
MT0020125 | Chinook WWTF | Activated Sludge-Oxidation Ditch; Optimized through mixers, DO probe, and SCADA [Nitrogen] | NA | 0.055 | 18.348 | 1.2935 | 17.0545 | 6224.8801 | 9.6327 | 8.7153 | 3181.0845 | 3043.7956
MT0021938 | City of Kalispell Advanced Wastewater Treatment and Biological Nutrient Removal Facility | Modified Johannesburg BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 2.85 | 950.76 | 185.8736 | 764.8864 | 279183.5433 | 499.149 | 451.611 | 164838.015 | 114345.5283
MT0022594 | Missoula WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 6.9 | 2301.84 | 554.168 | 1747.672 | 637900.2873 | 1208.466 | 1093.374 | 399081.51 | 238818.7773
NY0027561 | LeRoy R Summerson WWTF (City of Cortland) | Cycling Air and Adding Internal Carbon Source [Phosphorus, Nitrogen] | NA | 5.46 | 831.0393 | 376.1307 | 454.9086 | 166041.6521 | 732.2253 | 98.814 | 36067.1056 | 129974.5465
IL0028053 | Stickney WRP | Ostara Phosphorus Recovery [Phosphorus] | A/O or BNR 2-Stage Retrofit | 679 | 226514.4 | 53570.6556 | 172943.7444 | 63124466.706 | 46435.452 | 180078.948 | 65728816.02 | -2604349.314
MN0020567 | Monticello WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 1.15 | 647.2007 | 83.5376 | 563.6631 | 205737.0205 | 201.411 | 445.7897 | 162713.2332 | 43023.7873
MN0055361 | Plainview Township WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 0.755 | 228.0665 | 68.697 | 159.3695 | 58169.8591 | 132.2307 | 95.8358 | 34980.0575 | 23189.8016
MT0022568 | Billings WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 19.7 | 6571.92 | 1128.7273 | 5443.1927 | 1986765.3501 | 2888.3588 | 3683.5612 | 1344499.8234 | 642265.5267
MT0022608 | Bozeman WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 5.96 | 1988.256 | 305.1973 | 1683.0587 | 614316.427 | 884.7739 | 1103.4821 | 402770.9592 | 211545.4678
MT0020435 | Livingston WRF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 0.73 | 243.528 | 18.7517 | 224.7763 | 82043.3656 | 167.669 | 75.859 | 27688.5248 | 54354.8408
MT0020079 | Conrad WWTF | Extended Aeration Activated Sludge [Phosphorus] | A/O or BNR 2-Stage Replace | 0.191 | 63.7176 | 10.3541 | 53.3635 | 19477.6738 | 33.4517 | 30.2659 | 11047.0389 | 8430.6349
MN0050725 | Kasson WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 0.812 | 264.382 | 68.398 | 195.984 | 71534.1582 | 142.2137 | 122.1683 | 44591.438 | 26942.7203
WI0020478 | City of Sun Prairie WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 3.53 | 1177.608 | 499.8946 | 677.7134 | 247365.3925 | 618.2442 | 559.3638 | 204167.787 | 43197.6055
MN0020117 | Central Iron Range Sanitary District WWTF | Sequencing Batch Reactors [Phosphorus] | A/O or BNR 2-Stage Replace | 0.8 | 191.9534 | 45.1027 | 146.8507 | 53600.5128 | 140.112 | 51.8414 | 18922.1256 | 34678.3872
PA0080314 | Hampden Township WWTP | Added Process Control System [Nitrogen] | NA | 3.354 | 1118.8944 | 122.7987 | 996.0957 | 363574.945 | 587.4196 | 531.4748 | 193988.3166 | 169586.6284
MA0100153 | Town of Lee WWTF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 0.726 | 242.1936 | 22.7056 | 219.488 | 80113.1018 | 127.1516 | 115.042 | 41990.3154 | 38122.7864

## Loading Design Flow
NPDES Number | Facility Name | Nutrient Removal Project and [Target Nutrient(s)] | Upgraded Treatment System Type and Retrofit or Replace for Cost Estimation Purposes (select from dropdown) | Design Flow (MGD) | Design Flow Daily Influent TN (as N) Loading | Average Daily Effluent TN (as N) Loading Post-Project | Average lbs/day TN (as N) Removed Post-Project | Average Annual TN (as N) Removed (lbs) Post-Project | Average Daily Effluent TN (as N) Loading Pre-Project | Average lbs/day TN (as N) Removed Pre-Project | Average Annual TN (as N) Removed Pre- Project (lbs) Pre-Project | Average Annual TN (as N) Removed as a Result of Nutrient Removal Project based on Design Flow
IA0029025 | City of Atlantic WWTP | BNR [Total Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 8.1 | 2233.3352 | 293.8599 | 1939.4753 | 707908.4991 | 1418.634 | 814.7012 | 297365.9526 | 410542.5465
MN0020192 | Detroit Lakes WRF | Membrane Bioreactor with Bio-P [Phosphorus] | NA | 2.21 | 747.3933 | 163.8551 | 583.5381 | 212991.4153 | 457.4673 | 289.9259 | 105822.9615 | 107168.4537
MN0030066 | New Ulm WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 6.77 | 1809.0361 | 586.0735 | 1222.9626 | 446381.3446 | 1185.6978 | 623.3383 | 227518.4693 | 218862.8753
MN0040878 | St. Cloud NEW RF | Full Nitrification and BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 17.9 | 7019.4277 | 2060.1468 | 4959.2809 | 1810137.5358 | 3135.006 | 3884.4217 | 1417813.9278 | 392323.608
MN0066079 | City of Long Prairie WWTF | Extended Aeration Activated Sludge/BNR [Phosphorus] | A/O or BNR 2-Stage Replace | 2.279 | 1262.8158 | 343.2639 | 919.5519 | 335636.4387 | 859.3001 | 403.5156 | 147283.2078 | 188353.2309
MT0020125 | Chinook WWTF | Activated Sludge-Oxidation Ditch; Optimized through mixers, DO probe, and SCADA [Nitrogen] | NA | 0.5 | 166.8 | 11.7594 | 155.0406 | 56589.819 | 87.57 | 79.23 | 28918.95 | 27670.869
MT0021938 | City of Kalispell Advanced Wastewater Treatment and Biological Nutrient Removal Facility | Modified Johannesburg BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 5.4 | 1801.44 | 352.1815 | 1449.2585 | 528979.3452 | 945.756 | 855.684 | 312324.66 | 216654.6852
MT0022594 | Missoula WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 12 | 4003.2 | 963.7704 | 3039.4296 | 1109391.804 | 2101.68 | 1901.52 | 694054.8 | 415337.004
NY0027561 | LeRoy R Summerson WWTF (City of Cortland) | Cycling Air and Adding Internal Carbon Source [Phosphorus, Nitrogen] | NA | 9 | 1369.845 | 619.9956 | 749.8494 | 273695.031 | 1206.9648 | 162.8802 | 59451.273 | 214243.758
IL0028053 | Stickney WRP | Ostara Phosphorus Recovery [Phosphorus] | A/O or BNR 2-Stage Retrofit | 1440 | 480384 | 113610.816 | 366773.184 | 133872212.16 | 98478.72 | 381905.28 | 139395427.2 | -5523215.04
MN0020567 | Monticello WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 2.36 | 1328.1684 | 171.4337 | 1156.7346 | 422208.1465 | 413.3304 | 914.838 | 333915.8525 | 88292.294
MN0055361 | Plainview Township WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 2.67 | 806.5397 | 242.9417 | 563.598 | 205713.2766 | 467.6238 | 338.9159 | 123704.3093 | 82008.9672
MT0022568 | Billings WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 26 | 8673.6 | 1489.6908 | 7183.9092 | 2622126.858 | 3812.0472 | 4861.5528 | 1774466.772 | 847660.086
MT0022608 | Bozeman WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 8.5 | 2835.6 | 435.2646 | 2400.3354 | 876122.421 | 1261.842 | 1573.758 | 574421.67 | 301700.751
MT0020435 | Livingston WRF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 0.913 | 304.5768 | 23.4524 | 281.1244 | 102610.401 | 209.7011 | 94.8757 | 34629.6207 | 67980.7803
MT0020079 | Conrad WWTF | Extended Aeration Activated Sludge [Phosphorus] | A/O or BNR 2-Stage Replace | 0.5 | 166.8 | 27.105 | 139.695 | 50988.675 | 87.57 | 79.23 | 28918.95 | 22069.725
MN0050725 | Kasson WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 2.07 | 673.9788 | 174.3644 | 499.6144 | 182359.2458 | 362.5398 | 311.439 | 113675.2175 | 68684.0283
WI0020478 | City of Sun Prairie WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 7.53 | 2512.008 | 1066.3474 | 1445.6606 | 527666.1205 | 1318.8042 | 1193.2038 | 435519.387 | 92146.7335
MN0020117 | Central Iron Range Sanitary District WWTF | Sequencing Batch Reactors [Phosphorus] | A/O or BNR 2-Stage Replace | 2.5 | 599.8545 | 140.946 | 458.9085 | 167501.6025 | 437.85 | 162.0045 | 59131.6425 | 108369.96
PA0080314 | Hampden Township WWTP | Added Process Control System [Nitrogen] | NA | 5.69 | 1898.184 | 208.3257 | 1689.8583 | 616798.2817 | 996.5466 | 901.6374 | 329097.651 | 287700.6307
MA0100153 | Town of Lee WWTF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 1.5 | 500.4 | 46.9125 | 453.4875 | 165522.9375 | 262.71 | 237.69 | 86756.85 | 78766.0875

## Estimated Capital Cost
NPDES Number | Facility Name | Nutrient Removal Project and Target Nutrient(s) | Upgraded Treatment System Type and Retrofit or Replace for Cost Estimation Purposes (select from dropdown) | Facility-Supplied Estimated Capital Cost of Upgrade | Percent of Facility-Supplied Estimated Upgrade Capital Cost Attributed to Nutrient Removal Project | Estimated Capital Cost of Nutrient Removal Project | Facility-Supplied Estimated Capital Cost Year (select from dropdown) | Estimated Capital Cost of Nutrient Removal Project from Facility-Supplied Costs (2023$, MN) | Estimated Annualized Capital Cost of Nutrient Removal Project from Facility-Supplied Costs (2023$, MN) | Estimated Capital Cost of Nutrient Removal Project | Model-Estimated Capital Cost Year | Estimated Capital Cost of Nutrient Removal Project from Modeled Costs (2023$, MN) | Estimated Annualized Capital Cost of Nutrient Removal Project from Modeled Costs (2023$, MN) | Notes | Estimated Annualized Capital Cost
IA0029025 | City of Atlantic WWTP | BNR [Total Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 14000000 | 100% | 14000000 | 2012 | 24081740.664 | 1472760.2258 |  |  |  |  | Total capital cost of upgrades provided by facility; conservatively assumed that 100% of upgrade cost reported by facility attributed to nutrient removal | 1472760.2258 | 8.1 | 2372454.36 | 7.5 | 10 | 2239233 | 2794322 | 9489816.4 | 7.5 | 10 | 8956930 | 11177290 | 10403931.72 | 7.5 | 10 | 9685485 | 12679013 | 18958986.56 | 7.5 | 10 | 17583050 | 23316119
MN0020192 | Detroit Lakes WRF | Membrane Bioreactor with Bio-P [Phosphorus] | NA | 34000000 | 12% | 4080000 | 2019 | 5446987.0004 | 333119.8486 |  |  |  |  | Percent of capital cost attributed to nutrient removal project estimated based on conservative estimate from CapdetWorks cost model | 333119.8486 | 2.21 | 798244.4285 | 1 | 2.5 | 358586.4577 | 903617 | 3192979.3273 | 1 | 2.5 | 1434345.8308 | 3614470 | 3787941.4465 | 1 | 2.5 | 2049056.4821 | 4204699 | 6703896.784 | 1 | 2.5 | 3487924.5034 | 7474667
MN0030066 | New Ulm WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 1500000 | 100% | 1500000 | 2006 | 2687112.7153 | 164334.9949 |  |  |  |  | Total capital cost of upgrades provided by facility; percent of capital cost attributed to nutrient removal project estimated based on conservative estimate from CapdetWorks model | 164334.9949 | 6.77 | 2065978.304 | 5 | 7.5 | 1645895 | 2239233 | 8263911.8 | 5 | 7.5 | 6583580 | 8956930 | 9032185.808 | 5 | 7.5 | 7448159 | 9685485 | 16385381.048 | 5 | 7.5 | 13481444 | 17583050
MN0040878 | St. Cloud NEW RF | Full Nitrification and BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 23400000 | 100% | 23400000 | 2010 | 37540962.8191 | 2295882.0813 |  |  |  |  | Capital cost reported by facility for BNR and additional secondary clarifiers; 100% of this cost attributed to nutrient removal | 2295882.0813 | 17.9 | 4420856.16 | 10 | 20 | 2794322 | 4853226 | 17683425.06 | 10 | 20 | 11177290 | 19412904 | 19844498.65 | 10 | 20 | 12679013 | 21749248 | 36367280.03 | 10 | 20 | 23316119 | 39836576
MN0066079 | City of Long Prairie WWTF | Extended Aeration Activated Sludge/BNR [Phosphorus] | A/O or BNR 2-Stage Replace | 14000000 | 100% | 14000000 | 2020 | 18737150.3304 | 1145902.6212 |  |  |  |  | Total capital cost of upgrades provided by facility; conservatively assumed that 100% of upgrade cost reported by facility attributed to nutrient removal | 1145902.6212 | 2.279 | 823315.8334 | 1 | 2.5 | 358586.4577 | 903617 | 3293265.0391 | 1 | 2.5 | 1434345.8308 | 3614470 | 3887101.0024 | 1 | 2.5 | 2049056.4821 | 4204699 | 6887286.9388 | 1 | 2.5 | 3487924.5034 | 7474667
MT0020125 | Chinook WWTF | Activated Sludge-Oxidation Ditch; Optimized through mixers, DO probe, and SCADA [Nitrogen] | NA | 68000 | 100% | 68000 | 2004 | 164701.9344 | 10072.6298 |  |  |  |  | No major infrastructure changes; addition of mixers, DO probe, and SCADA only; cost provided by facility | 10072.6298 | 0.5 | 217720.8863 | 0.5 | 0.75 | 217720.8863 | 285220.4402 | 870883.5453 | 0.5 | 0.75 | 870883.5453 | 1140881.7606 | 1430332.9331 | 0.5 | 0.75 | 1430332.9331 | 1732403.5823 | 2429081.5134 | 0.5 | 0.75 | 2429081.5134 | 2946726.0729
MT0021938 | City of Kalispell Advanced Wastewater Treatment and Biological Nutrient Removal Facility | Modified Johannesburg BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 21712500 | 50% | 10856250 | 2009 | 21186899.8881 | 1295721.2644 |  |  |  |  | Capital cost provided by facility for upgrade and expansion of existing plant; conservatively assuming 50% of the capital cost attributed to nutrient removal technology upgrade. | 1295721.2644 | 5.4 | 1740829.08 | 5 | 7.5 | 1645895 | 2239233 | 6963316 | 5 | 7.5 | 6583580 | 8956930 | 7806131.16 | 5 | 7.5 | 7448159 | 9685485 | 14137700.96 | 5 | 7.5 | 13481444 | 17583050
MT0022594 | Missoula WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 14000000 | 100% | 14000000 | 2000 | 40844655.6219 | 2497925.0908 |  |  |  |  | Capital cost provided by facility for upgrade of existing activated sludge system to BNR and addition of new BNR treatment units | 2497925.0908 | 12 | 3206102.8 | 10 | 20 | 2794322 | 4853226 | 12824412.8 | 10 | 20 | 11177290 | 19412904 | 14493060 | 10 | 20 | 12679013 | 21749248 | 26620210.4 | 10 | 20 | 23316119 | 39836576
NY0027561 | LeRoy R Summerson WWTF (City of Cortland) | Cycling Air and Adding Internal Carbon Source [Phosphorus, Nitrogen] | NA | 0 | 100% | 0 | 2022 | 0 | 0 |  |  |  |  | There were no infrastructure changes at the facility; the faciltiy has been able to achieve consistently greater nutrient removal through reprogramming the SCADA system to cycle air in and off in the tanks and selectively bypassing the gravity clarifier to increase carbon to the tanks | 0 | 9 | 2572286.4 | 7.5 | 10 | 2239233 | 2794322 | 10289146 | 7.5 | 10 | 8956930 | 11177290 | 11481601.8 | 7.5 | 10 | 9685485 | 12679013 | 21022891.4 | 7.5 | 10 | 17583050 | 23316119
IL0028053 | Stickney WRP | Ostara Phosphorus Recovery [Phosphorus] | A/O or BNR 2-Stage Retrofit | 35000000 | 100% | 35000000 | 2019 | 45496956.6919 | 2782444.556 |  |  |  |  | Facility-supplied capital cost for the Ostara phosphorus recovery system | 2782444.556 | 1440 | #VALUE! | 50 | #VALUE! | 10334334 | #VALUE! | #VALUE! | 50 | #VALUE! | 41337335 | #VALUE! | #VALUE! | 50 | #VALUE! | 47608053 | #VALUE! | #VALUE! | 50 | #VALUE! | 87008214 | #VALUE!
MN0020567 | Monticello WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | [6 empty] | 4003505.6983 | 2022 | 4554472.5432 | 278536.5935 | No information on cost or year of upgrade provided; estimated cost based on modeled cost to upgrade by BNR 3- 5-Stage retrofit | 278536.5935 | 2.36 | 852747.4827 | 1 | 2.5 | 358586.4577 | 903617 | 3410991.7442 | 1 | 2.5 | 1434345.8308 | 3614470 | 4003505.6983 | 1 | 2.5 | 2049056.4821 | 4204699 | 7102571.0337 | 1 | 2.5 | 3487924.5034 | 7474667
MN0055361 | Plainview Township WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 500000 | 100% | 500000 | 2006 | 895704.2384 | 54778.3316 |  |  |  |  | Capital cost reported by facility for biological phosphorus removal upgrade; conservatively assumed that 100% of the reported capital cost is for nitrogen removal | 54778.3316 | 2.67 | 954091.904 | 2.5 | 5 | 903617 | 1645895 | 3816369.48 | 2.5 | 5 | 3614470 | 6583580 | 4425254.28 | 2.5 | 5 | 4204699 | 7448159 | 7883127.836 | 2.5 | 5 | 7474667 | 13481444
MT0022568 | Billings WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 70000000 | 70% | 49000000 | 2017 | 82715060.2937 | 5058581.6271 |  |  |  |  | Capital cost reported by facilty for upgrades based on a need to increase basin volume; assumed that 70% of the upgrade capital cost is attributed to nutrient removal (somewhat conservative estimate based on comparison to model). | 5058581.6271 | 26 | 6017320.8 | 20 | 30 | 4853226 | 6793384 | 24069283.8 | 20 | 30 | 19412904 | 27173537 | 27384610.6 | 20 | 30 | 21749248 | 31141519 | 49884392 | 20 | 30 | 39836576 | 56582936
MT0022608 | Bozeman WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 45000000 | 35% | 15750000 | 2012 | 27956595.2123 | 1709733.6131 |  |  |  |  | In addition to 2012 upgrade capital cost, a cost of $54,000,000 was incurred in 2007 to upgrade existing conventional activated sludge system to BNR; this additional cost is included in the unit cost calculations ($/lb TN (as N) removed) but is not shown here; estimated percent of capital cost attributed to upgrade based on approximate percentage of total treatment system cost attributed to nutrient removal treatment technology by CapdetWorks cost model; assumes upgrade of all treatment units to increase capacity and performance and, therefore, only a percentage of total cost attributed to nutrient removal | 1709733.6131 | 8.5 | 2461268.6 | 7.5 | 10 | 2239233 | 2794322 | 9845074 | 7.5 | 10 | 8956930 | 11177290 | 10882896.2 | 7.5 | 10 | 9685485 | 12679013 | 19876277.6 | 7.5 | 10 | 17583050 | 23316119
MT0020435 | Livingston WRF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 20000000 | 25% | 5000000 | 2019 | 7882451.4633 | 482064.8623 |  |  |  |  | Total capital cost of upgrades provided by facility; percent of capital cost attributed to nutrient removal project estimated based on conservative estimate from CapdetWorks model | 482064.8623 | 0.913 | 333055.0836 | 0.75 | 1 | 285220.4402 | 358586.4577 | 1332220.3344 | 0.75 | 1 | 1140881.7606 | 1434345.8308 | 1938861.2729 | 0.75 | 1 | 1732403.5823 | 2049056.4821 | 3299587.4496 | 0.75 | 1 | 2946726.0729 | 3487924.5034
MT0020079 | Conrad WWTF | Extended Aeration Activated Sludge [Phosphorus] | A/O or BNR 2-Stage Replace | 4193000 | 25% | 1048250 | 2010 | 1985864.1956 | 121448.9368 |  |  |  |  | Total capital cost of upgrade from lagoons to activated sludge provided by facility; percent of capital cost attributed to nutrient removal project estimated as 25% of total cost | 121448.9368 | 0.5 | 217720.8863 | 0.5 | 0.75 | 217720.8863 | 285220.4402 | 870883.5453 | 0.5 | 0.75 | 870883.5453 | 1140881.7606 | 1430332.9331 | 0.5 | 0.75 | 1430332.9331 | 1732403.5823 | 2429081.5134 | 0.5 | 0.75 | 2429081.5134 | 2946726.0729
MN0050725 | Kasson WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | [6 empty] | 2989501.0715 | 2022 | 3400919.4875 | 207989.0745 | No capital cost information provided by the facility; estimated cost based on modeled cost to upgrade by addition of BNR 2-Stage | 207989.0745 | 2.07 | 747374.9112 | 1 | 2.5 | 358586.4577 | 903617 | 2989501.0715 | 1 | 2.5 | 1434345.8308 | 3614470 | 3586748.1449 | 1 | 2.5 | 2049056.4821 | 4204699 | 6331800.8176 | 1 | 2.5 | 3487924.5034 | 7474667
WI0020478 | City of Sun Prairie WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | [6 empty] | 2245894.068 | 2022 | 2554976.4727 | 156253.976 | No capital cost information provided by the facility. Estimated cost based on modeled cost to upgrade by retrofit to BNR 2-Stage | 156253.976 | 7.53 | 2245894.068 | 7.5 | 10 | 2239233 | 2794322 | 8983574.32 | 7.5 | 10 | 8956930 | 11177290 | 9721407.336 | 7.5 | 10 | 9685485 | 12679013 | 17651846.828 | 7.5 | 10 | 17583050 | 23316119
MN0020117 | Central Iron Range Sanitary District WWTF | Sequencing Batch Reactors [Phosphorus] | A/O or BNR 2-Stage Replace | [6 empty] | 3614470 | 2022 | 4111897.3254 | 251470.1457 | No capital cost information provided by the facility. Estimated cost based on modeled cost to upgrade by replacing with BNR 2-Stage | 251470.1457 | 2.5 | 903617 | 2.5 | 5 | 903617 | 1645895 | 3614470 | 2.5 | 5 | 3614470 | 6583580 | 4204699 | 2.5 | 5 | 4204699 | 7448159 | 7474667 | 2.5 | 5 | 7474667 | 13481444
PA0080314 | Hampden Township WWTP | Added Process Control System [Nitrogen] | NA | 0 | 100% | 0 | 2010 | 0 | 0 |  |  |  |  | No capital cost provided by facility; assumed no cost attributed to nutrient removal | 0 | 5.69 | 1809656.288 | 5 | 7.5 | 1645895 | 2239233 | 7238624.6 | 5 | 7.5 | 6583580 | 8956930 | 8065660.976 | 5 | 7.5 | 7448159 | 9685485 | 14613487.256 | 5 | 7.5 | 13481444 | 17583050
MA0100153 | Town of Lee WWTF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 12000000 | 25% | 3000000 | 2000 | 7154157.0717 | 437524.7675 |  |  |  |  | Total capital cost of upgrades provided by facility; percent of capital cost attributed to nutrient removal project estimated based on estimate from CapdetWorks | 437524.7675 | 1.5 | 540263.3051 | 1 | 2.5 | 358586.4577 | 903617 | 2161053.8872 | 1 | 2.5 | 1434345.8308 | 3614470 | 2767603.9881 | 1 | 2.5 | 2049056.4821 | 4204699 | 4816838.6689 | 1 | 2.5 | 3487924.5034 | 7474667
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[17 empty] | Modeled Ohio-2022 |  |  |  |  | Interpolated-Ohio 2022
[17 empty] | A/O or BNR 2-Stage Retrofit | A/O or BNR 2-Stage Replace | A2O or BNR 3- to 5-Stage Retrofit | A2O or BNR 3- to 5-Stage Replace
[16 empty] | 0.5 | 217720.8863 | 870883.5453 | 1430332.9331 | 2429081.5134 |  |  |  | A/O or BNR 2-Stage Retrofit | A/O or BNR 2-Stage Replace | A2O or BNR 3- to 5-Stage Retrofit | A2O or BNR 3- to 5-Stage Replace
[16 empty] | 0.75 | 285220.4402 | 1140881.7606 | 1732403.5823 | 2946726.0729 |  | Enter Flow | x | 7.7 | 7.7 | 7.7 | 7.7
[16 empty] | 1 | 358586.4577 | 1434345.8308 | 2049056.4821 | 3487924.5034 |  | Capital Cost | y | 2283640.12 | 9134558.8 | 9924967.24 | 18041695.52
[16 empty] | 2.5 | 903617 | 3614470 | 4204699 | 7474667 |  |  | x1 | 7.5 | 7.5 | 7.5 | 7.5
[16 empty] | 5 | 1645895 | 6583580 | 7448159 | 13481444 |  |  | x2 | 10 | 10 | 10 | 10
[16 empty] | 7.5 | 2239233 | 8956930 | 9685485 | 17583050 |  |  | y1 | 2239233 | 8956930 | 9685485 | 17583050
[16 empty] | 10 | 2794322 | 11177290 | 12679013 | 23316119 |  |  | y2 | 2794322 | 11177290 | 12679013 | 23316119
[16 empty] | 20 | 4853226 | 19412904 | 21749248 | 39836576
[16 empty] | 30 | 6793384 | 27173537 | 31141519 | 56582936
[16 empty] | 40 | 8634434 | 34537735 | 39888668 | 72705999
[16 empty] | 50 | 10334334 | 41337335 | 47608053 | 87008214

## Estimated O&M Cost
NPDES Number | Facility Name | Nutrient Removal Project and Target Nutrient(s) | Upgraded Treatment System Type and Retrofit or Replace for Cost Estimation Purposes (select from dropdown) | Facility-Supplied O&M Cost Attributed to Nutrient Removal Project | Facility-Supplied O&M Cost Year (select from dropdown) | Facility-Supplied Annual O&M Cost for Nutrient Removal Project (2023$, MN) | Facility-Supplied Pre-Upgrade O&M Cost | Facility-Supplied Pre-Upgrade O&M Cost Year (select from dropdown) | Facility-Supplied Post-Upgrade Annual O&M Cost | Facility-Supplied Post-Upgrade O&M Cost Year (select from dropdown) | Facility-Supplied Pre-Project Annual O&M Cost (2023$, MN) | Facility-Supplied Post-Project Annual O&M Cost (2023$, MN) | Percent of Upgrade O&M Cost Attributed to Nutrient Removal Project | Facility-Supplied Annual O&M Cost for Nutrient Removal Project (2023$, MN) | Model-Estimated Nutrient Removal Project O&M Cost | Model-Estimated O&M Cost Year | Model Estimated Annual O&M Cost for Nutrient Removal Project (2023$, MN) | Notes | System | Flow | Total | Percentage | Estimated O&M Cost
IA0029025 | City of Atlantic WWTP | BNR [Total Nitrogen] | A2O or BNR 3- to 5-Stage Replace | [11 empty] | 401694.7907 | 2022 | 494890.5598 | No O&M cost information provided by facility | 3 | 10 | 13 | 0.13682 | 494890.5598 | 7.7 | 2706750.36 | 7.5 | 10 | 2665819 | 3177461 | 2935848.8 | 7.5 | 10 | 2892140 | 3438500
MN0020192 | Detroit Lakes WRF | Membrane Bioreactor with Bio-P [Phosphorus] | NA |  |  |  | 650000 | 2023 | 1000000 | 2024 | 650000 | 978841.7817 | 40% | 131536.7127 |  |  |  | Post-project O&M cost based on estimate from facility; pre-project O&M cost and % of upgrade O&M cost attributed to nutrient removal project based on estimates from CapdetWorks | 3 | 10 | 13 | 0.13682 | 131536.7127 | 1.08 | 997600.8667 | 1 | 2.5 | 972687 | 1439822 | 1097930.2667 | 1 | 2.5 | 1073354 | 1534159
MN0030066 | New Ulm WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | [11 empty] | 51601.8698 | 2022 | 63573.8347 | No O&M cost information provided by facility | 1 | 10 | 11 | 0.03746 | 63573.8347 | 2.3 | 1377537.3333 | 1 | 2.5 | 972687 | 1439822 | 1472718.3333 | 1 | 2.5 | 1073354 | 1534159
MN0040878 | St. Cloud NEW RF | Full Nitrification and BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | [11 empty] | 466881.3256 | 2022 | 575200.7891 | No O&M cost information provided by facility | 3 | 10 | 13 | 0.13682 | 575200.7891 | 9.88 | 3152902.184 | 7.5 | 10 | 2665819 | 3177461 | 3412274.72 | 7.5 | 10 | 2892140 | 3438500
MN0066079 | City of Long Prairie WWTF | Extended Aeration Activated Sludge/BNR [Phosphorus] | A/O or BNR 2-Stage Replace | [11 empty] | 39469.4746 | 2022 | 48626.6459 | No O&M cost information provided by facility | 1 | 10 | 11 | 0.03746 | 48626.6459 | 1.26 | 1053657.0667 | 1 | 2.5 | 972687 | 1439822 | 1153226.8667 | 1 | 2.5 | 1073354 | 1534159
MT0020125 | Chinook WWTF | Activated Sludge-Oxidation Ditch; Optimized through mixers, DO probe, and SCADA [Nitrogen] | NA |  |  |  | 18000 | 2016 | 0 | 2016 | 24726.6812 | 0 | 100% | -24726.6812 |  |  |  | Negative O&M cost based on reported energy cost savings (before and after installation of new equipment) | 3 | 10 | 13 | 0.13682 | -24726.6812 | 0.5 | 777994 | 0.5 | 0.75 | 777994 | 872861 | 864078 | 0.5 | 0.75 | 864078 | 977121
MT0021938 | City of Kalispell Advanced Wastewater Treatment and Biological Nutrient Removal Facility | Modified Johannesburg BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 0 | 2009 | 0 | [11 empty] | Facility reports no significant change in O&M cost following upgrade; assume no O&M cost due to change in nutrient removal technology | 3 | 10 | 13 | 0.13682 | 0 | 2.85 | 1530536.68 | 2.5 | 5 | 1439822 | 2087784 | 1639959.52 | 2.5 | 5 | 1534159 | 2289877
MT0022594 | Missoula WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | [11 empty] | 375937.3963 | 2022 | 463157.2845 | No O&M cost information provided by facility | 3 | 10 | 13 | 0.13682 | 463157.2845 | 6.9 | 2527090.6 | 5 | 7.5 | 2087784 | 2665819 | 2747596.88 | 5 | 7.5 | 2289877 | 2892140
NY0027561 | LeRoy R Summerson WWTF (City of Cortland) | Cycling Air and Adding Internal Carbon Source [Phosphorus, Nitrogen] | NA | 0 | 2022 | 0 | [11 empty] | The facility reports no change in O&M costs after operational changes to improve nutrient removal | 3 | 10 | 13 | 0.13682 | 0 | 5.46 | 2194142.44 | 5 | 7.5 | 2087784 | 2665819 | 2400693.392 | 5 | 7.5 | 2289877 | 2892140
IL0028053 | Stickney WRP | Ostara Phosphorus Recovery [Phosphorus] | A/O or BNR 2-Stage Retrofit | 13100000 | 2022 | 13715651.8822 | [11 empty] | Facility-supplied O&M cost; not clear how much is attributable to the phosphorus recovery system | 1 | 30 | 31 | 0.025727 | 13715651.8822 | 679 | #VALUE! | 50 | #VALUE! | 10928370 | #VALUE! | #VALUE! | 50 | #VALUE! | 11506100 | #VALUE!
MN0020567 | Monticello WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | [11 empty] | 153165.5878 | 2022 | 188700.987 | No O&M cost information provided by facility | 3 | 10 | 13 | 0.13682 | 188700.987 | 1.15 | 1019400.5 | 1 | 2.5 | 972687 | 1439822 | 1119434.5 | 1 | 2.5 | 1073354 | 1534159
MN0055361 | Plainview Township WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | [11 empty] | 32771.7316 | 2022 | 40374.9837 | No O&M cost information provided by facility | 1 | 10 | 11 | 0.03746 | 40374.9837 | 0.755 | 874857.52 | 0.75 | 1 | 872861 | 972687 | 979045.66 | 0.75 | 1 | 977121 | 1073354
MT0022568 | Billings WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | [11 empty] | 675224.5612 | 2022 | 831880.9923 | No O&M cost information provided by facility | 3 | 30 | 33 | 0.12242 | 831880.9923 | 19.7 | 5185243.63 | 10 | 20 | 3177461 | 5247340 | 5515842.3 | 10 | 20 | 3438500 | 5580090
MT0022608 | Bozeman WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | [11 empty] | 344953.4634 | 2022 | 424984.8805 | No O&M cost information provided by facility | 3 | 10 | 13 | 0.13682 | 424984.8805 | 5.96 | 2309749.44 | 5 | 7.5 | 2087784 | 2665819 | 2521145.992 | 5 | 7.5 | 2289877 | 2892140
MT0020435 | Livingston WRF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | [11 empty] | 132456.3148 | 2022 | 163187.0298 | O&M cost estimate consistent with facility estimate of $1 million total O&M cost and CapdetWorks cost model estimate of 3.75% of the total O&M cost attributable to the nutrient removal technology | 3 | 10 | 13 | 0.13682 | 163187.0298 | 0.73 | 865271.64 | 0.5 | 0.75 | 777994 | 872861 | 968077.56 | 0.5 | 0.75 | 864078 | 977121
MT0020079 | Conrad WWTF | Extended Aeration Activated Sludge [Phosphorus] | A/O or BNR 2-Stage Replace | [11 empty] | 29143.2719 | 2022 | 35904.698 | No O&M cost information provided by the facility; O&M cost estimate at design flow of 0.5 MGD, which is the lowest cost used in the model | 1 | 10 | 11 | 0.03746 | 35904.698 | 0.5 | 777994 | 0.5 | 0.75 | 777994 | 872861 | 864078 | 0.5 | 0.75 | 864078 | 977121
MN0050725 | Kasson WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | [11 empty] | 33624.3223 | 2022 | 41425.3808 | No O&M cost information provided by the facility; facility indicates that 2015 upgrades were estimated to save $17,000 in annual electricity costs. | 1 | 10 | 11 | 0.03746 | 41425.3808 | 0.812 | 897617.848 | 0.75 | 1 | 872861 | 972687 | 1000986.784 | 0.75 | 1 | 977121 | 1073354
WI0020478 | City of Sun Prairie WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | [11 empty] | 63935.2256 | 2022 | 78768.6082 | No O&M cost information provided by the facility | 1 | 10 | 11 | 0.03746 | 78768.6082 | 3.53 | 1706782.344 | 2.5 | 5 | 1439822 | 2087784 | 1845514.816 | 2.5 | 5 | 1534159 | 2289877
MN0020117 | Central Iron Range Sanitary District WWTF | Sequencing Batch Reactors [Phosphorus] | A/O or BNR 2-Stage Replace | [11 empty] | 33444.8295 | 2022 | 41204.2446 | No O&M cost information provided by the facility | 1 | 10 | 11 | 0.03746 | 41204.2446 | 0.8 | 892826.2 | 0.75 | 1 | 872861 | 972687 | 996367.6 | 0.75 | 1 | 977121 | 1073354
PA0080314 | Hampden Township WWTP | Added Process Control System [Nitrogen] | NA | 0 | 2023 | 0 | [11 empty] | No O&M cost provided by facility; assumed no cost attributed to nutrient removal (potentially O&M savings) | 3 | 10 | 13 | 0.13682 | 0 | 3.354 | 1661165.8192 | 2.5 | 5 | 1439822 | 2087784 | 1792312.2688 | 2.5 | 5 | 1534159 | 2289877
MA0100153 | Town of Lee WWTF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | [11 empty] | 132208.8427 | 2022 | 162882.1426 | No O&M cost information provided by the facility | 3 | 10 | 13 | 0.13682 | 162882.1426 | 0.726 | 863753.768 | 0.5 | 0.75 | 777994 | 872861 | 966268.872 | 0.5 | 0.75 | 864078 | 977121
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | 0 | 0 | 0 |  |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[27 empty] | Modeled-Ohio 2022 |  |  |  | Interpolated-Ohio 2022
[27 empty] | 2-Stage BNR |  | 3- to 5-Stage BNR |  |  |  | 2-Stage BNR |  | 3- to 5-Stage BNR
[24 empty] | 0.5 |  |  | 777994 |  | 864078 |  | Enter Flow | x | 7.7 |  | 7.7
[24 empty] | 0.75 |  |  | 872861 |  | 977121 |  | O&M Cost | y | 2706750.36 |  | 2935848.8
[24 empty] | 1 |  |  | 972687 |  | 1073354 |  |  | x1 | 7.5 |  | 7.5
[24 empty] | 2.5 |  |  | 1439822 |  | 1534159 |  |  | x2 | 10 |  | 10
[24 empty] | 5 |  |  | 2087784 |  | 2289877 |  |  | y1 | 2665819 |  | 2892140
[24 empty] | 7.5 |  |  | 2665819 |  | 2892140 |  |  | y2 | 3177461 |  | 3438500
[24 empty] | 10 |  |  | 3177461 |  | 3438500
[24 empty] | 20 |  |  | 5247340 |  | 5580090
[24 empty] | 30 |  |  | 7256650 |  | 7674780
[24 empty] | 40 |  |  | 9162220 |  | 9700420
[24 empty] | 50 |  |  | 10928370 |  | 11506100

## Incremental Capital OH 2022 (hidden)
|  | Estimated Upgrade Cost | Total Estimated Capital Cost of Treatment System | % of Total Cost Attributed to Upgrade
Types | 0.5
NA | A/O or BNR 2-Stage Retrofit | 217720.8863 | 9430000 | 2.309%
A/O or BNR 2-Stage Retrofit | A/O or BNR 2-Stage Replace | 870883.5453 | 9430000 | 9.235%
A/O or BNR 2-Stage Replace | A2O or BNR 3- to 5-Stage Retrofit | 1430332.9331 | 10200000 | 14.02%
A2O or BNR 3- to 5-Stage Retrofit | A2O or BNR 3- to 5-Stage Replace | 2429081.5134 | 10200000 | 23.81%
A2O or BNR 3- to 5-Stage Replace
0.75
| A/O or BNR 2-Stage Retrofit | 285220.4402 | 11000000 | 2.593%
| A/O or BNR 2-Stage Replace | 1140881.7606 | 11000000 | 10.37%
| A2O or BNR 3- to 5-Stage Retrofit | 1732403.5823 | 12000000 | 14.44%
| A2O or BNR 3- to 5-Stage Replace | 2946726.0729 | 12000000 | 24.56%
1
| A/O or BNR 2-Stage Retrofit | 358586.4577 | 13300000 | 2.696%
| A/O or BNR 2-Stage Replace | 1434345.8308 | 13300000 | 10.78%
| A2O or BNR 3- to 5-Stage Retrofit | 2049056.4821 | 14300000 | 14.33%
| A2O or BNR 3- to 5-Stage Replace | 3487924.5034 | 14300000 | 24.39%
2.5
| A/O or BNR 2-Stage Retrofit | 903617 | 22500000 | 4.016%
| A/O or BNR 2-Stage Replace | 3614470 | 22500000 | 16.06%
| A2O or BNR 3- to 5-Stage Retrofit | 4204699 | 24100000 | 17.45%
| A2O or BNR 3- to 5-Stage Replace | 7474667 | 24100000 | 31.02%
5
| A/O or BNR 2-Stage Retrofit | 1645895 | 33700000 | 4.884%
| A/O or BNR 2-Stage Replace | 6583580 | 33700000 | 19.54%
| A2O or BNR 3- to 5-Stage Retrofit | 7448159 | 38200000 | 19.5%
| A2O or BNR 3- to 5-Stage Replace | 13481444 | 38200000 | 35.29%
7.5
| A/O or BNR 2-Stage Retrofit | 2239233 | 43600000 | 5.136%
| A/O or BNR 2-Stage Replace | 8956930 | 43600000 | 20.54%
| A2O or BNR 3- to 5-Stage Retrofit | 9685485 | 48500000 | 19.97%
| A2O or BNR 3- to 5-Stage Replace | 17583050 | 48500000 | 36.25%
10
| A/O or BNR 2-Stage Retrofit | 2794322 | 51800000 | 5.394%
| A/O or BNR 2-Stage Replace | 11177290 | 51800000 | 21.58%
| A2O or BNR 3- to 5-Stage Retrofit | 12679013 | 59600000 | 21.27%
| A2O or BNR 3- to 5-Stage Replace | 23316119 | 59600000 | 39.12%
20
| A/O or BNR 2-Stage Retrofit | 4853226 | 87900000 | 5.521%
| A/O or BNR 2-Stage Replace | 19412904 | 87900000 | 22.09%
| A2O or BNR 3- to 5-Stage Retrofit | 21749248 | 99200000 | 21.92%
| A2O or BNR 3- to 5-Stage Replace | 39836576 | 99200000 | 40.16%
30
| A/O or BNR 2-Stage Retrofit | 6793384 | 124000000 | 5.479%
| A/O or BNR 2-Stage Replace | 27173537 | 124000000 | 21.91%
| A2O or BNR 3- to 5-Stage Retrofit | 31141519 | 140000000 | 22.24%
| A2O or BNR 3- to 5-Stage Replace | 56582936 | 140000000 | 40.42%
40
| A/O or BNR 2-Stage Retrofit | 8634434 | 156000000 | 5.535%
| A/O or BNR 2-Stage Replace | 34537735 | 156000000 | 22.14%
| A2O or BNR 3- to 5-Stage Retrofit | 39888668 | 181000000 | 22.04%
| A2O or BNR 3- to 5-Stage Replace | 72705999 | 181000000 | 40.17%
50
| A/O or BNR 2-Stage Retrofit | 10334334 | 181000000 | 5.71%
| A/O or BNR 2-Stage Replace | 41337335 | 181000000 | 22.84%
| A2O or BNR 3- to 5-Stage Retrofit | 47608053 | 213000000 | 22.35%
| A2O or BNR 3- to 5-Stage Replace | 87008214 | 213000000 | 40.85%

## Interpolation of Capital Costs (hidden)
| A/O or BNR 2-Stage Retrofit | A/O or BNR 2-Stage Replace | A2O or BNR 3- to 5-Stage Retrofit | A2O or BNR 3- to 5-Stage Replace | Interpolated-Ohio 2022
0.5 | 217720.8863 | 870883.5453 | 1430332.9331 | 2429081.5134
0.75 | 285220.4402 | 1140881.7606 | 1732403.5823 | 2946726.0729 |  |  | A/O or BNR 2-Stage Retrofit | A/O or BNR 2-Stage Replace | A2O or BNR 3- to 5-Stage Retrofit | A2O or BNR 3- to 5-Stage Replace
1 | 358586.4577 | 1434345.8308 | 2049056.4821 | 3487924.5034 | Enter Flow | x | 8.5 | 6.5 | 6.5 | 8.5
2.5 | 903617 | 3614470 | 4204699 | 7474667 | Capital Cost | y | 2461268.6 | 8007590 | 8790554.6 | 19876277.6
5 | 1645895 | 6583580 | 7448159 | 13481444 |  | x1 | 7.5 | 5 | 5 | 7.5
7.5 | 2239233 | 8956930 | 9685485 | 17583050 |  | x2 | 10 | 7.5 | 7.5 | 10
10 | 2794322 | 11177290 | 12679013 | 23316119 |  | y1 | 2239233 | 6583580 | 7448159 | 17583050
20 | 4853226 | 19412904 | 21749248 | 39836576 |  | y2 | 2794322 | 8956930 | 9685485 | 23316119
30 | 6793384 | 27173537 | 31141519 | 56582936
40 | 8634434 | 34537735 | 39888668 | 72705999
50 | 10334334 | 41337335 | 47608053 | 87008214

## Incremental O&M OH 2022 (hidden)
O&M Cost Components--BNR Upgrade Only
|  | Operation ($/yr) | Maintenance ($/yr) | Material ($/yr) | Chemical ($/yr) | Energy ($/yr) | Total ($/yr) | O&M Cost After Upgrade | Upgrade O&M Cost ($/1,000 gal.) | Fraction to Apply to O&M Wage Adjustment Factor | Fraction to Apply to Energy Adjustment Factor | % of Total O&M Costs Attributable to Upgrade
[14 empty] | Averages | Averages
Types | 0.5 | [12 empty] | 0.67066 | 0.32934
NA | A/O or BNR 2-Stage | 18500 | 6600 | 0 | 0 | 5200 | 30300 | 777994 | 60.6 | 0.82838 | 0.17162 | 3.895% |  | 0.52081 | 0.47919
A/O or BNR 2-Stage Retrofit | A2O or BNR 3- to 5-Stage | 63800 | 35500 | 13250 | 0 | 12100 | 124650 | 864078 | 249.3 | 0.89138 | 0.10862 | 14.43% |  | 0.59574 | 0.40426
A/O or BNR 2-Stage Replace
A2O or BNR 3- to 5-Stage Retrofit | 0.75
A2O or BNR 3- to 5-Stage Replace | A/O or BNR 2-Stage | 20600 | 7400 | 0 | 0 | 4000 | 32000 | 872861 | 42.6667 | 0.875 | 0.125 | 3.666%
| A2O or BNR 3- to 5-Stage | 71500 | 39600 | 15700 | 0 | 15700 | 142500 | 977121 | 190 | 0.87618 | 0.12382 | 14.58%
1
| A/O or BNR 2-Stage | 22200 | 8200 | 0 | 0 | 6900 | 37300 | 972687 | 37.3 | 0.81501 | 0.18499 | 3.835%
| A2O or BNR 3- to 5-Stage | 72600 | 40800 | 17900 | 0 | 21400 | 152700 | 1073354 | 152.7 | 0.84125 | 0.15875 | 14.23%
2.5
| A/O / BNR 2-Stage | 33900 | 13000 | 0 | 0 | 13300 | 60200 | 1439822 | 24.08 | 0.77907 | 0.22093 | 4.181%
| A2O / BNR 3- to 5-Stage | 74900 | 43200 | 30450 | 0 | 52500 | 201050 | 1534159 | 80.42 | 0.69226 | 0.30774 | 13.1%
5
| A/O / BNR 2-Stage | 40000 | 15800 | 0 | 0 | 19000 | 74800 | 2087784 | 14.96 | 0.74599 | 0.25401 | 3.583%
| A2O / BNR 3- to 5-Stage | 94000 | 51500 | 61500 | 0 | 100000 | 307000 | 2289877 | 61.4 | 0.59267 | 0.40733 | 13.41%
7.5
| A/O or BNR 2-Stage | 48000 | 20100 | 0 | 0 | 33000 | 101100 | 2665819 | 13.48 | 0.67359 | 0.32641 | 3.792%
| A2O or BNR 3- to 5-Stage | 98000 | 56300 | 77000 | 0 | 151500 | 382800 | 2892140 | 51.04 | 0.50458 | 0.49542 | 13.24%
10
| A/O or BNR 2-Stage | 48000 | 20900 | 0 | 0 | 35000 | 103900 | 3177461 | 10.39 | 0.66314 | 0.33686 | 3.27%
| A2O or BNR 3- to 5-Stage | 96000 | 55900 | 91000 | 0 | 197000 | 439900 | 3438500 | 43.99 | 0.43537 | 0.56463 | 12.79%
20
| A/O or BNR 2-Stage | 58000 | 27000 | 0 | 0 | 65000 | 150000 | 5247340 | 7.5 | 0.56667 | 0.43333 | 2.859%
| A2O or BNR 3- to 5-Stage | 106000 | 62000 | 136000 | 0 | 390000 | 694000 | 5580090 | 34.7 | 0.30108 | 0.69892 | 12.44%
30
| A/O or BNR 2-Stage | 65000 | 30000 | 0 | 0 | 80000 | 175000 | 7256650 | 5.8333 | 0.54286 | 0.45714 | 2.412%
| A2O or BNR 3- to 5-Stage | 114000 | 66000 | 175000 | 0 | 575000 | 930000 | 7674780 | 31 | 0.23841 | 0.76159 | 12.12%
40
| A/O or BNR 2-Stage | 72000 | 35000 | 0 | 0 | 130000 | 237000 | 9162220 | 5.925 | 0.45148 | 0.54852 | 2.587%
| A2O or BNR 3- to 5-Stage | 113000 | 68000 | 214500 | 0 | 780000 | 1175500 | 9700420 | 29.3875 | 0.18835 | 0.81165 | 12.12%
50
| A/O or BNR 2-Stage | 77000 | 39000 | 0 | 0 | 150000 | 266000 | 10928370 | 5.32 | 0.43609 | 0.56391 | 2.434%
| A2O or BNR 3- to 5-Stage | 123000 | 72000 | 249500 | 0 | 970000 | 1414500 | 11506100 | 28.29 | 0.16738 | 0.83262 | 12.29%
[12 empty] | 3.319% | Averages:
13.16%
[12 empty] | 3.746% | Average if < 10 MGD
13.68%
[12 empty] | 2.573% | Average if > 10 MGD
12.24%

## Interpolation of O&M Costs (hidden)
| Modeled-Ohio 2022 |  | Interpolated-Ohio 2022
| 2-Stage BNR | 3- to 5-Stage BNR |  |  | 2-Stage BNR | 3- to 5-Stage BNR
0.5 | 777994 | 864078 | Enter Flow | x | 7.7 | 7.7
0.75 | 872861 | 977121 | O&M Cost | y | 2706750.36 | 2935848.8
1 | 972687 | 1073354 |  | x1 | 7.5 | 7.5
2.5 | 1439822 | 1534159 |  | x2 | 10 | 10
5 | 2087784 | 2289877 |  | y1 | 2665819 | 2892140
7.5 | 2665819 | 2892140 |  | y2 | 3177461 | 3438500
10 | 3177461 | 3438500
20 | 5247340 | 5580090
30 | 7256650 | 7674780
40 | 9162220 | 9700420
50 | 10928370 | 11506100

## Adjustment (hidden)
Year | CWCCIS Index for 19 - Buildings, Grounds, and Utilities | Implicit Price Deflator | State | CWCCIS State Adjustment Factor | BLS OEWS Median Annual Wage for Water and Wastewater Treatment Plant and System Operators (May 2023) | Average Price of Electricity to Commercial Customers for 2023 (Cents per kWh)
NA |  |  | NA
2000 | 468.05 | 72.722 | Alabama | 0.92 | 22.47 | 13.18 | 1.4183 | 0.9393
2001 | 472.18 | 74.36 | Alaska | 1.16 | 37.19 | 20.81 | 0.85695 | 0.59491
2002 | 486.16 | 75.515 | Arizona | 0.96 | 26.5 | 11.74 | 1.2026 | 1.0545
2003 | 497.4 | 77.006 | Arkansas | 0.88 | 18.82 | 10.34 | 1.6934 | 1.1973
2004 | 563.78 | 79.077 | California | 1.24 | 38.04 | 23.91 | 0.8378 | 0.51777
2005 | 605.47 | 81.556 | Colorado | 0.93 | 30.23 | 11.67 | 1.0543 | 1.0608
2006 | 645.52 | 84.071 | Connecticut | 1.15 | 35.87 | 19.98 | 0.88849 | 0.61962
2007 | 681.88 | 86.349 | Delaware | 1.1 | 27.43 | 11.92 | 1.1619 | 1.0386
2008 | 741.36 | 88.013 | District of Columbia | 1.03 | NA | 17.01 | #VALUE! | 0.72781
2009 | 699.7 | 88.556 | Florida | 0.91 | 25.06 | 11.83 | 1.2717 | 1.0465
2010 | 720.8 | 89.632 | Georgia | 0.93 | 22.98 | 11.4 | 1.3869 | 1.086
2011 | 758.79 | 91.481 | Hawaii | 1.21 | 31.21 | 39.38 | 1.0211 | 0.31437
2012 | 769.3 | 93.185 | Idaho | 1.01 | 23.08 | 8.82 | 1.3808 | 1.4036
2013 | 776.44 | 94.771 | Illinois | 1.14 | 33.21 | 11.4 | 0.95965 | 1.086
2014 | 791.59 | 96.421 | Indiana | 0.97 | 24.43 | 12.54 | 1.3045 | 0.98724
2015 | 786.32 | 97.316 | Iowa | 0.97 | 27.35 | 10.42 | 1.1653 | 1.1881
2016 | 782.46 | 98.241 | Kansas | 0.94 | 22.09 | 11.11 | 1.4427 | 1.1143
2017 | 808.93 | 100 | Kentucky | 0.96 | 22.65 | 11.49 | 1.4071 | 1.0775
2018 | 841.84 | 102.291 | Louisiana | 0.91 | 18.92 | 10.3 | 1.6845 | 1.2019
2019 | 866.18 | 104.008 | Maine | 1.02 | 24.06 | 17.92 | 1.3246 | 0.69085
2020 | 864.03 | 105.381 | Maryland | 1 | 25.16 | 12.82 | 1.2667 | 0.96568
2021 | 993.48 | 110.213 | Massachusetts | 1.15 | 30.93 | 19.28 | 1.0304 | 0.64212
2022 | 1151.34 | 117.973 | Michigan | 1.02 | 27.15 | 13.34 | 1.1738 | 0.92804
2023 | 1156.39 | 122.273 | Minnesota | 1.11 | 31.87 | 12.38 | 1 | 1
2024 | 1178.15 | 124.916 | Mississippi | 0.9 | 19.84 | 12.36 | 1.6064 | 1.0016
|  |  | Missouri | 0.98 | 23.61 | 10.2 | 1.3499 | 1.2137
|  |  | Montana | 0.94 | 27.63 | 12.03 | 1.1535 | 1.0291
|  |  | Nebraska | 0.94 | 24.59 | 9.2 | 1.2961 | 1.3457
|  |  | Nevada | 1.08 | 38.59 | 11.79 | 0.82586 | 1.05
|  |  | New Hampshire | 1.04 | 26.93 | 20.32 | 1.1834 | 0.60925
|  |  | New Jersey | 1.23 | 33.66 | 14.15 | 0.94682 | 0.87491
|  |  | New Mexico | 0.91 | 21.15 | 10.98 | 1.5069 | 1.1275
|  |  | New York | 1.17 | 29.8 | 18.06 | 1.0695 | 0.68549
|  |  | North Carolina | 0.89 | 23.3 | 9.86 | 1.3678 | 1.2556
|  |  | North Dakota | 0.95 | 25.67 | 7.66 | 1.2415 | 1.6162
|  |  | Ohio | 0.98 | 26.25 | 10.76 | 1.2141 | 1.1506
|  |  | Oklahoma | 0.9 | 18.39 | 9.39 | 1.733 | 1.3184
|  |  | Oregon | 1.07 | 30.37 | 10.29 | 1.0494 | 1.2031
|  |  | Pennsylvania | 1.08 | 28.62 | 11.25 | 1.1136 | 1.1004
|  |  | Rhode Island | 1.14 | 27.73 | 17.52 | 1.1493 | 0.70662
|  |  | South Carolina | 0.92 | 23.1 | 10.59 | 1.3797 | 1.169
|  |  | South Dakota | 0.94 | 25 | 10.04 | 1.2748 | 1.2331
|  |  | Tennessee | 0.9 | 23.32 | 11.82 | 1.3666 | 1.0474
|  |  | Texas | 0.88 | 22.07 | 8.96 | 1.444 | 1.3817
|  |  | Utah | 0.96 | 26.54 | 8.52 | 1.2008 | 1.4531
|  |  | Vermont | 1.01 | 27.68 | 17.94 | 1.1514 | 0.69008
|  |  | Virginia | 0.94 | 23.89 | 9.23 | 1.334 | 1.3413
|  |  | Washington | 1.08 | 37.65 | 10.08 | 0.84648 | 1.2282
|  |  | West Virginia | 1.01 | 20.8 | 11.05 | 1.5322 | 1.1204
|  |  | Wisconsin | 1.06 | 28.51 | 12.69 | 1.1179 | 0.97557
|  |  | Wyoming | 0.95 | 25.35 | 9.79 | 1.2572 | 1.2646

## Unit Cost Actual Flow
NPDES Number | Facility Name | Nutrient Removal Project and Target Nutrient(s) | Upgraded Treatment System Type and Retrofit or Replace for Cost Estimation Purposes (select from dropdown) | Average Flow (MGD) | Estimated Total Annual Cost Attributed to TN Removal (2023$, MN) | Annual TN (as N) Removed (lbs.) as a Result of Nutrient Removal Project Based on Average Flow | Estimated Annual Cost/lb TN (as N) Removed Based on Average Flow | Notes
IA0029025 | City of Atlantic WWTP | BNR [Total Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 7.7 | 1967650.7855 | 390268.8405 | 5.0418
MN0020192 | Detroit Lakes WRF | Membrane Bioreactor with Bio-P [Phosphorus] | NA | 1.08 | 464656.5613 | 52371.914 | 8.8722
MN0030066 | New Ulm WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 2.3 | 227908.8296 | 74355.1866 | 3.0651
MN0040878 | St. Cloud NEW RF | Full Nitrification and BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 9.88 | 2871082.8703 | 216545.0976 | 13.2586
MN0066079 | City of Long Prairie WWTF | Extended Aeration Activated Sludge/BNR [Phosphorus] | A/O or BNR 2-Stage Replace | 1.26 | 1194529.2672 | 104135.6169 | 11.4709
MT0020125 | Chinook WWTF | Activated Sludge-Oxidation Ditch; Optimized through mixers, DO probe, and SCADA [Nitrogen] | NA | 0.055 | -14654.0514 | 3043.7956 | -4.8144
MT0021938 | City of Kalispell Advanced Wastewater Treatment and Biological Nutrient Removal Facility | Modified Johannesburg BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 2.85 | 1295721.2644 | 114345.5283 | 11.3316
MT0022594 | Missoula WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 6.9 | 2961082.3753 | 238818.7773 | 12.3989
NY0027561 | LeRoy R Summerson WWTF (City of Cortland) | Cycling Air and Adding Internal Carbon Source [Phosphorus, Nitrogen] | NA | 5.46 | 0 | 129974.5465 | 0
IL0028053 | Stickney WRP | Ostara Phosphorus Recovery [Phosphorus] | A/O or BNR 2-Stage Retrofit | 679 | 16498096.4381 | -2604349.314 | -6.3348 | Effluent TN concentration has increased since phosphorus recovery technology brought online in 2019
MN0020567 | Monticello WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 1.15 | 467237.5806 | 43023.7873 | 10.86
MN0055361 | Plainview Township WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 0.755 | 95153.3153 | 23189.8016 | 4.1032
MT0022568 | Billings WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 19.7 | 5890462.6194 | 642265.5267 | 9.1714
MT0022608 | Bozeman WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 5.96 | 4780106.4936 | 211545.4678 | 22.5961 | Estimated total annual cost and annual cost/lb TN (as N) removed is based on both the 2007 and 2012 upgrades.
MT0020435 | Livingston WRF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 0.73 | 645251.8921 | 54354.8408 | 11.8711
MT0020079 | Conrad WWTF | Extended Aeration Activated Sludge [Phosphorus] | A/O or BNR 2-Stage Replace | 0.191 | 157353.6348 | 8430.6349 | 18.6645 | O&M cost estimate calculated at design flow of 0.5 MGD, which is the lowest cost used in the model
MN0050725 | Kasson WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 0.812 | 249414.4553 | 26942.7203 | 9.2572
WI0020478 | City of Sun Prairie WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 3.53 | 235022.5842 | 43197.6055 | 5.4406
MN0020117 | Central Iron Range Sanitary District WWTF | Sequencing Batch Reactors [Phosphorus] | A/O or BNR 2-Stage Replace | 0.8 | 292674.3903 | 34678.3872 | 8.4397
PA0080314 | Hampden Township WWTP | Added Process Control System [Nitrogen] | NA | 3.354 | 0 | 169586.6284 | 0 | Assumed no cost attributed to nutrient removal (potentially O&M savings)
MA0100153 | Town of Lee WWTF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 0.726 | 600406.9101 | 38122.7864 | 15.7493

## Unit Cost Design Flow
NPDES Number | Facility Name | Nutrient Removal Project and Target Nutrient(s) | Upgraded Treatment System Type and Retrofit or Replace for Cost Estimation Purposes (select from dropdown) | Design Flow (MGD) | Estimated Total Annual Cost Attributed to TN Removal (2023$, MN) | Annual TN (as N) Removed (lbs.) as a Result of Nutrient Removal Project Based on Design Flow | Estimated Annual Cost/lb TN (as N) Removed Based on Design Flow | Notes
IA0029025 | City of Atlantic WWTP | BNR [Total Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 8.1 | 1993359.386 | 410542.5465 | 4.8554
MN0020192 | Detroit Lakes WRF | Membrane Bioreactor with Bio-P [Phosphorus] | NA | 2.21 | 602282.9366 | 107168.4537 | 5.62
MN0030066 | New Ulm WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 6.77 | 351463.1952 | 218862.8753 | 1.6059
MN0040878 | St. Cloud NEW RF | Full Nitrification and BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 17.9 | 3337996.8712 | 392323.608 | 8.5083
MN0066079 | City of Long Prairie WWTF | Extended Aeration Activated Sludge/BNR [Phosphorus] | A/O or BNR 2-Stage Replace | 2.279 | 1233855.1022 | 188353.2309 | 6.5508
MT0020125 | Chinook WWTF | Activated Sludge-Oxidation Ditch; Optimized through mixers, DO probe, and SCADA [Nitrogen] | NA | 0.5 | -14654.0514 | 27670.869 | -0.52958 | Assumes no additional O&M cost savings at design flow
MT0021938 | City of Kalispell Advanced Wastewater Treatment and Biological Nutrient Removal Facility | Modified Johannesburg BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 5.4 | 1295721.2644 | 216654.6852 | 5.9806
MT0022594 | Missoula WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 12 | 3303416.0204 | 415337.004 | 7.9536
NY0027561 | LeRoy R Summerson WWTF (City of Cortland) | Cycling Air and Adding Internal Carbon Source [Phosphorus, Nitrogen] | NA | 9 | 0 | 214243.758 | 0
IL0028053 | Stickney WRP | Ostara Phosphorus Recovery [Phosphorus] | A/O or BNR 2-Stage Retrofit | 1440 | 31870130.4327 | -5523215.04 | -5.7702 | Effluent TN concentration has increased since phosphorus recovery technology brought online in 2019
MN0020567 | Monticello WWTP | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Retrofit | 2.36 | 665783.8365 | 88292.294 | 7.5407
MN0055361 | Plainview Township WWTP | Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 2.67 | 197561.3865 | 82008.9672 | 2.409
MT0022568 | Billings WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 26 | 6156495.627 | 847660.086 | 7.2629
MT0022608 | Bozeman WRF | BNR [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 8.5 | 4961224.2111 | 301700.751 | 16.4442 | Estimated total annual cost and annual cost/lb TN (as N) removed is based on both the 2007 and 2012 upgrades.
MT0020435 | Livingston WRF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 0.913 | 686160.4215 | 67980.7803 | 10.0934
MT0020079 | Conrad WWTF | Extended Aeration Activated Sludge [Phosphorus] | A/O or BNR 2-Stage Replace | 0.5 | 157353.6348 | 22069.725 | 7.1298 | O&M cost estimate calculated at design flow of 0.5 MGD, which is the lowest cost used in the model; therefore there was no adjustment of O&M cost when estimating the unit cost at design flow
MN0050725 | Kasson WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Replace | 2.07 | 313593.1857 | 68684.0283 | 4.5657
WI0020478 | City of Sun Prairie WWTP | Activated sludge with Biological Phosphorus Removal [Phosphorus] | A/O or BNR 2-Stage Retrofit | 7.53 | 324278.7975 | 92146.7335 | 3.5192
MN0020117 | Central Iron Range Sanitary District WWTF | Sequencing Batch Reactors [Phosphorus] | A/O or BNR 2-Stage Replace | 2.5 | 380233.4101 | 108369.96 | 3.5087
PA0080314 | Hampden Township WWTP | Added Process Control System [Nitrogen] | NA | 5.69 | 0 | 287700.6307 | 0 | Assumed no cost attributed to nutrient removal (potentially O&M savings)
MA0100153 | Town of Lee WWTF | Sequencing Batch Reactors [Phosphorus, Nitrogen] | A2O or BNR 3- to 5-Stage Replace | 1.5 | 774058.12 | 78766.0875 | 9.8273