## Pump Cal - Circular
Date calculated:
Directions:
Input Values - yellow boxes
Diameter | 10 | feet | Area | 78.5 | square feet |  |  | Output Calculations - green boxes
Pumping Rate
Drawdown | 2 | foot | Drawdown | 1174.36 | gallons
Distance |  | inches | Volume
Drawdown | 5 | minutes | Drawdown | 230.2667 | gallons/minute
Time | 6 | seconds | Rate
Refill | 2 | foot | Refill | 1174.36 | gallons |  |  |  | Drawdown or
Distance |  | inches | Volume | [5 empty] | Refill Distance
Refill | 7 | minutes | Refill | 163.1056 | gallons/minute
Time | 12 | seconds | Rate
Pumping Rate = |  | 393.3722 | gallons/minute
***For a more accurate number, calibrate each pump at least three times:
| Trial #1 |  | 192.2 |  | gallons/minute
| Trial #2 |  | 193.5 |  | gallons/minute
| Trial #3 |  | 191.4 |  | gallons/minute
| Average |  | 192.3667 |  | gallons/minute
Diameter
Diameter
Pump Calibration - Circular Wet Well
Wastewater Permit Program
Doc Type: Course Material