## Pump Cal - Rectangular
Date calculated:
Directions:
Input Values - yellow boxes
Length | 17.8 | feet |  |  |  |  | Output Calculations - green boxes
Width | 5 | feet | Area | 89 | square feet |  | Pumping Rate
Drawdown | 1 | foot | Drawdown | 998.58 | gallons
Distance | 6 | inches | Volume
Drawdown | 2 | minutes | Drawdown | 374.4675 | gallons/minute |  |  | Drawdown or
Time | 40 | seconds | Rate |  |  |  |  | Refill Distance
Refill | 1 | foot | Refill | 998.58 | gallons
Distance | 6 | inches | Volume
Refill | 86 | minutes | Refill | 11.6114 | gallons/minute
Time | 0 | seconds | Rate
Pumping Rate = |  | 386.0789 | gallons/minute
***For a more accurate number, calibrate each pump at least three times
| Trial #1 |  | 125.7 | gallons/minute
| Trial #2 |  | 108 | gallons/minute
| Trial #3 |  | 134 | gallons/minute
| Average |  | 122.5667 | gallons/minute
Pump Calibration - Rectangular Wet Well
Wastewater Permit Program
Doc Type: Course Material
Length
Width