## Pump Readings-Hr-Independent
Facility: | [7 empty] | Directions
Input numbers
Month/year: |  | Pump calibration date: | [6 empty] | Output calculations
Average monthly flow
Note: 1. On the first day, you will need to input the hours between the last reading in the previous month and the first reading this month. 2. Every day must have a pump reading. 3. Use this spreadsheet if your third meter runs only when both pumps are running together.
Calibrated Pump Capacity in gallons per minute:
| Pump #1 | 226 |  | Pump #2 | 226 |  |  |  | Pump #1 and #2 together | 230
| Pump #1 |  |  | Pump #2 |  |  | Pump #1 + #2 (third meter) |  |  | Total Flow
Day of | Meter | Hours* | Flow | Meter | Hours* | Flow | Meter | Hours* | Flow
Month | Reading | see note | (gallons) | Reading | see note | (gallons) | Reading | see note | (gallons) | (gallons)
1 | 2534.4 | 0.7 | 9492 | 2568.9 | 0.7 | 9492 | 2540 | 0 | 0 | 18984
2 | 2535.2 | 0.8 | 10848 | 2569.6 | 0.7 | 9492 | 2540.2 | 0.2 | 2760 | 23100
3 | 2535.9 | 0.7 | 9492 | 2570.2 | 0.6 | 8136 | 2541 | 0.8 | 11040 | 28668
4 | 2536.6 | 0.7 | 9492 | 2570.9 | 0.7 | 9492 | 2541 | 0 | 0 | 18984
5 | 2537.3 | 0.7 | 9492 | 2571.6 | 0.7 | 9492 | 2541 | 0 | 0 | 18984
6 | 2538 | 0.7 | 9492 | 2572.3 | 0.7 | 9492 | 2541 | 0 | 0 | 18984
7 | 2538.8 | 0.8 | 10848 | 2573 | 0.7 | 9492 | 2541 | 0 | 0 | 20340
8 | 2539.6 | 0.8 | 10848 | 2573.7 | 0.7 | 9492 | 2541 | 0 | 0 | 20340
9 | 2540.4 | 0.8 | 10848 | 2574.4 | 0.7 | 9492 | 2541 | 0 | 0 | 20340
10 | 2541.2 | 0.8 | 10848 | 2575.2 | 0.8 | 10848 | 2541 | 0 | 0 | 21696
11 | 2542 | 0.8 | 10848 | 2576 | 0.8 | 10848 | 2541.5 | 0.5 | 6900 | 28596
12 | 2542.8 | 0.8 | 10848 | 2576.7 | 0.7 | 9492 | 2541.5 | 0 | 0 | 20340
13 | 2543.5 | 0.7 | 9492 | 2577.4 | 0.7 | 9492 | 2541.5 | 0 | 0 | 18984
14 | 2544.2 | 0.7 | 9492 | 2578.1 | 0.7 | 9492 | 2541.5 | 0 | 0 | 18984
15 | 2544.9 | 0.7 | 9492 | 2578.8 | 0.7 | 9492 | 2541.5 | 0 | 0 | 18984
16 | 2545.6 | 0.7 | 9492 | 2579.5 | 0.7 | 9492 | 2541.5 | 0 | 0 | 18984
17 | 2546.3 | 0.7 | 9492 | 2580.3 | 0.8 | 10848 | 2542 | 0.5 | 6900 | 27240
18 | 2547 | 0.7 | 9492 | 2581.1 | 0.8 | 10848 | 2542 | 0 | 0 | 20340
19 | 2547.7 | 0.7 | 9492 | 2581.8 | 0.7 | 9492 | 2542 | 0 | 0 | 18984
20 | 2548.4 | 0.7 | 9492 | 2582.5 | 0.7 | 9492 | 2542 | 0 | 0 | 18984
21 | 2549.1 | 0.7 | 9492 | 2583.2 | 0.7 | 9492 | 2542 | 0 | 0 | 18984
22 | 2549.8 | 0.7 | 9492 | 2583.9 | 0.7 | 9492 | 2542 | 0 | 0 | 18984
23 | 2550.4 | 0.6 | 8136 | 2584.5 | 0.6 | 8136 | 2542 | 0 | 0 | 16272
24 | 2551 | 0.6 | 8136 | 2585.1 | 0.6 | 8136 | 2542 | 0 | 0 | 16272
25 | 2551.6 | 0.6 | 8136 | 2585.7 | 0.6 | 8136 | 2542.7 | 0.7 | 9660 | 25932
26 | 2552.2 | 0.6 | 8136 | 2586.4 | 0.7 | 9492 | 2543 | 0.3 | 4140 | 21768
27 | 2553 | 0.8 | 10848 | 2587.2 | 0.8 | 10848 | 2543 | 0 | 0 | 21696
28 | 2553.8 | 0.8 | 10848 | 2588 | 0.8 | 10848 | 2543 | 0 | 0 | 21696
29 | 2554 | 0.2 | 2712 | 2589 | 1 | 13560 | 2543 | 0 | 0 | 16272
30 | 2556 | 2 | 27120 | 2590 | 1 | 13560 | 2543 | 0 | 0 | 40680
31 | 2557 | 1 | 13560 | 2592 | 2 | 27120 | 2545 | 2 | 27600 | 68280
Column Totals = |  | 23.3 | 315948 |  | 23.8 | 322728 |  | 5 | 69000 | 707676
[8 empty] | Average Monthly Flow = | 22828.2581 | (gals/day)
Pump Readings - In Hours Use only when all meters run independent of each other Wastewater Permit Program Doc Type: Course Material