## Pump Readings-Min-Independent
Facility: | [7 empty] | Directions
Input numbers
Month/year: |  | Pump calibration date: | [6 empty] | Output calculations
Average monthly flow
Note: 1. On the first day, you will need to input the minutes between the last reading in the previous month and the first reading this month. 2. Every day must have a pump reading. 3. Use this spreadsheet if your third meter runs only when both pumps are running together.
Calibrated Pump Capacity in gallons per minute:
| Pump #1 | 226 |  | Pump #2 | 226 |  |  |  | Pump #1 and #2 together | 230
| Pump #1 |  |  | Pump #2 |  |  | Pump #1 + #2 (third meter) |  |  | Total Flow
Day of | Meter | Minutes* | Flow | Meter | Minutes* | Flow | Meter | Minutes* | Flow
Month | Reading | see note | (gallons) | Reading | see note | (gallons) | Reading | see note | (gallons) | (gallons)
1 | 2534.4 | 85.1 | 19232.6 | 2534.4 | 75.1 | 16972.6 | 2540 | 0 | 0 | 36205.2
2 | 2594.3 | 59.9 | 13537.4 | 2594.3 | 59.9 | 13537.4 | 2590.5 | 50.5 | 11615 | 38689.8
3 | 2684.2 | 89.9 | 20317.4 | 2684.2 | 89.9 | 20317.4 | 2590.5 | 0 | 0 | 40634.8
4 | 2745.3 | 61.1 | 13808.6 | 2745.3 | 61.1 | 13808.6 | 2590.5 | 0 | 0 | 27617.2
5 | 2875.8 | 130.5 | 29493 | 2875.8 | 130.5 | 29493 | 2590.5 | 0 | 0 | 58986
6 | 2956.3 | 80.5 | 18193 | 2956.3 | 80.5 | 18193 | 2590.5 | 0 | 0 | 36386
7 | 3056.5 | 100.2 | 22645.2 | 3056.5 | 100.2 | 22645.2 | 2590.5 | 0 | 0 | 45290.4
8 | 3125.6 | 69.1 | 15616.6 | 3125.6 | 69.1 | 15616.6 | 2590.5 | 0 | 0 | 31233.2
9 | 3189.5 | 63.9 | 14441.4 | 3189.5 | 63.9 | 14441.4 | 2605.3 | 14.8 | 3404 | 32286.8
10 | 3289.7 | 100.2 | 22645.2 | 3289.7 | 100.2 | 22645.2 | 2658.3 | 53 | 12190 | 57480.4
11 | 3368 | 78.3 | 17695.8 | 3368 | 78.3 | 17695.8 | 2658.3 | 0 | 0 | 35391.6
12 | 3458.9 | 90.9 | 20543.4 | 3458.9 | 90.9 | 20543.4 | 2658.3 | 0 | 0 | 41086.8
13 | 3524.7 | 65.8 | 14870.8 | 3524.7 | 65.8 | 14870.8 | 2658.3 | 0 | 0 | 29741.6
14 | 3602.8 | 78.1 | 17650.6 | 3602.8 | 78.1 | 17650.6 | 2658.3 | 0 | 0 | 35301.2
15 | 3710.3 | 107.5 | 24295 | 3710.3 | 107.5 | 24295 | 2658.3 | 0 | 0 | 48590
16 | 3845.6 | 135.3 | 30577.8 | 3845.6 | 135.3 | 30577.8 | 2658.3 | 0 | 0 | 61155.6
17 | 3956.9 | 111.3 | 25153.8 | 3956.9 | 111.3 | 25153.8 | 2658.3 | 0 | 0 | 50307.6
18 | 4036.3 | 79.4 | 17944.4 | 4036.3 | 79.4 | 17944.4 | 2682.5 | 24.2 | 5566 | 41454.8
19 | 4126.7 | 90.4 | 20430.4 | 4126.7 | 90.4 | 20430.4 | 2682.5 | 0 | 0 | 40860.8
20 | 4202.5 | 75.8 | 17130.8 | 4202.5 | 75.8 | 17130.8 | 2682.5 | 0 | 0 | 34261.6
21 | 4310.2 | 107.7 | 24340.2 | 4310.2 | 107.7 | 24340.2 | 2682.5 | 0 | 0 | 48680.4
22 | 4445.5 | 135.3 | 30577.8 | 4445.5 | 135.3 | 30577.8 | 2682.5 | 0 | 0 | 61155.6
23 | 4589.3 | 143.8 | 32498.8 | 4589.3 | 143.8 | 32498.8 | 2682.5 | 0 | 0 | 64997.6
24 | 4678.5 | 89.2 | 20159.2 | 4678.5 | 89.2 | 20159.2 | 2682.5 | 0 | 0 | 40318.4
25 | 4745.6 | 67.1 | 15164.6 | 4745.6 | 67.1 | 15164.6 | 2682.5 | 0 | 0 | 30329.2
26 | 4802.8 | 57.2 | 12927.2 | 4802.8 | 57.2 | 12927.2 | 2682.5 | 0 | 0 | 25854.4
27 | 4902.5 | 99.7 | 22532.2 | 4902.5 | 99.7 | 22532.2 | 2735.8 | 53.3 | 12259 | 57323.4
28 | 5012.8 | 110.3 | 24927.8 | 5012.8 | 110.3 | 24927.8 | 2735.8 | 0 | 0 | 49855.6
29 | 5147.9 | 135.1 | 30532.6 | 5147.9 | 135.1 | 30532.6 | 2735.8 | 0 | 0 | 61065.2
30 | 5247.1 | 99.2 | 22419.2 | 5247.1 | 99.2 | 22419.2 | 2735.8 | 0 | 0 | 44838.4
31 | 5347 | 99.9 | 22577.4 | 5347 | 99.9 | 22577.4 | 2800 | 64.2 | 14766 | 59920.8
Column Totals = |  | 2897.7 | 654880.2 |  | 2887.7 | 652620.2 |  | 260 | 59800 | 1367300.4
[8 empty] | Average Monthly Flow = | 44106.4645 | (gals/day)
Pump Readings - In Minutes
Use only when all meters run independent of each other
Wastewater Permit Program
Doc Type: Course Material