## Wasting Rate
Directions: | [7 empty] | Date calculated:
Input numbers - yellow boxes
Output calculations - green boxes
SRT - orange box
1. SRT | 25 | days
2. Influent Flow |  | 4.36 | MGD
3. Size of each aeration tank
| Length | 160 | feet | Width | 40 | feet | Water depth | 18 | feet | Volume | 0.8617 | MG
4. Total volume of all aeration tanks
| Number of aeration tanks |  |  | 4 |  | Total volume | 3.4468 | MG
5. Size of each final clarifier
| Diameter | 60 | feet | Water depth | 15 | feet | Volume | 0.31708 | MG
6. Total volume of all final clarifiers
| number of clarifiers |  | 2 |  | Total volume | 0.63415 | MG
7. Total volume of aeration tank(s) and final clarifier(s)
| 4.0809 | MG
8. MLSS or MLVSS concentration
| 3870 | mg/L
9. Waste sludge concentration
| 9000 | mg/L
10. Effluent TSS concentration
| 12 | mg/L
11. Calculated wasting rate
| 44.7075 | gpm
Wasting Rate Calculation Worksheet
Wastewater Permit Program
Doc Type: Course Material